## Info
분류 | 구분값 | 인버터 상태 의미 (Description)
Inverter Mode | 0x0000 | Wait / Initial (대기/초기화)
Inverter Mode | 0x0001 | Standby (스탠바이)
Inverter Mode | 0x0002 | Initialization (초기화 중)
Inverter Mode | 0x0003 | On-Grid / Normal (정상 발전 / 계통 연계)
Inverter Mode | 0x0004 | Off-Grid (독립 운전)
Inverter Mode | 0x0005 | Fault / Alarm (고장 발생)
Inverter Mode | 0x0006 | Flash / Update (펌웨어 업데이트 중)
Inverter Mode | 0x0007 | Derating (출력 제한 운전 중)
Inverter Mode | 0x0009 | Shutdown mode
분류 | 구분값 (Hex) | 국가 규격 (Regulation Standard)
Regulation Code | 0x0000 | Default (기본값)
Regulation Code | 0x0001 | VDE0126 (독일/유럽)
Regulation Code | 0x0002 | VDE-AR-N 4105 (독일)
Regulation Code | 0x0003 | AS4777 (호주)
Regulation Code | 0x0004 | CEI 0-21 (이탈리아)
Regulation Code | 0x000A | EN50438 (유럽 공통)
Regulation Code | 0x0022 | KOREA (한국 KSC 8564/8565 규격)
Type 기호 | 의미 | 메모리 크기 | 값의 범위 | 설명
U16 | 16-bit Unsigned Integer | 1 Word (1 Len) | 0 ~ 65,535 | 음수가 없는 일반적인 16비트 정수입니다.
S16 | 16-bit Signed Integer | 1 Word (1 Len) | -32,768 ~ 32,767 | 전류, 역률 등 음수(-)가 나올 수 있는 데이터입니다. 시스템 설정 시 반드시 'Signed'로 설정해야 합니다.
U32 | 32-bit Unsigned Integer | 2 Words (2 Len) | 0 ~ 약 42억 | 누적 발전량(Energy)처럼 숫자가 매우 커지는 데이터에 사용됩니다.
S32 | 32-bit Signed Integer | 2 Words (2 Len) | -약 21억 ~ 21억 | 음수가 포함된 매우 큰 숫자에 사용됩니다.
ASCII | 문자열 (String) | (길이에 따라 다름) | - | 시리얼 넘버, 펌웨어 버전 등 영문/숫자 텍스트 데이터입니다.
Bit | 1-bit 상태값 (Boolean) | 1 Word 내의 1칸 | 0 또는 1 | 알람(에러) 상태를 판별할 때 사용됩니다.
컬럼명 (Header) | 설명 (Description) | 실무 적용 팁
Category | 데이터의 그룹 분류 | 엑셀 필터 기능을 이용해 필요한 데이터만 모아볼 때 사용합니다.
Address | 16진수 통신 주소 | 인버터 매뉴얼 기준의 원본 주소입니다. (예: 0x1001)
Register Name | 데이터의 이름/항목 | 해당 주소가 의미하는 값입니다.
R/W | 읽기/쓰기 권한 | RO(Read Only): 상태를 읽기만 가능RW(Read/Write): 읽기 및 설정값 변경(제어) 가능
Type | 데이터 타입 (자료형) | 메모리 크기와 음수 표현 여부를 결정합니다. (아래 2번 항목 참조)
Len (Length) | 레지스터 사용 개수 | 통신으로 한 번에 읽어올 워드(Word, 16-bit)의 개수입니다.
Scale | 데이터 변환 배율 | 통신으로 들어온 원시 데이터(Raw)에 이 값을 곱해야 실제 값이 됩니다.
Unit | 물리적 단위 | V(전압), A(전류), W(전력), Hz(주파수) 등
Remarks | 비고 및 상태값 정의 | 특정 숫자가 의미하는 상태나(예: 0=대기, 1=가동), 알람의 정의를 나타냅니다.
분류 (Category) | 레지스터 순서 (16-bit) | 상위 8비트 (High Byte) 데이터 | 하위 8비트 (Low Byte) 데이터 | 비고 / 예시
History Log Data | Word 1 (예: 0xB600) | Year (연도, 0~99) | Month (월, 1~12) | 24년 4월 = 24, 04
History Log Data | Word 2 (예: 0xB601) | Day (일, 1~31) | Hour (시, 0~23) | 15일 14시 = 15, 14
History Log Data | Word 3 (예: 0xB602) | Minute (분, 0~59) | Event Code (알람/상태 코드) | 30분, 에러1 = 30, 01

## Protocol Map
Category | Address | Register Name | R/W | Type | Len | Scale | Unit | Remarks / Range
Device Info | 0x1A00 | Device Model name | RO | string | 8 |  | ASCII | Ex.：PV 30KTL
Device Info | 0x1A10 | Device Serial number | RO | string | 8 |  | ASCII | Ex.：1234-123456789
Device Info | 0x1A1C | Master firmware version | RO | string | 3 |  | ASCII | Ex.：123456
Device Info | 0x1A26 | Slave firmware version | RO | string | 3 |  | ASCII | Ex.：123456
Device Info | 0x1A3B | MPPT Number | RO | U16 | 1 |  |  | Ex.：1=1 MPPT
Device Info | 0x1A44 | Nominal Voltage | RO | U16 | 1 | 0.1 | V | Ex.：2200 = 220V For CN (NB/T 32004) regulation code (0x5101=0x0E), the unit is 10ms. Other regulation codes use 1ms.
Device Info | 0x1A45 | Nominal Frequency | RO | U16 | 1 | 0.01 | Hz | Ex.：5000 = 50Hz Only support for 3 phase model (0x1A48 = 3).
Device Info | 0x1A46 | Nominal Active Power (Low word) | RO | U16 | 1 | 1 | W | Ex.：1500 = 1500W
Device Info | 0x1A4E | Nominal Active Power (High word) | RO | U16 | 1 | 1 | W | Ex.：1 = (1*65536)W
Device Info | 0x1A48 | Grid Phase Number | RO | U16 | 1 |  |  | 1=single phase 2=split phase 3=three phases
Device Info | 0x1A60 | EMS Firmware Version | RO | string | 3 |  | ASCII | Ex.：123456
Device Info | 0x1A8E | LCD firmware version | RO | string | 3 |  | ASCII | Ex.：123456
Real Time Data | 0x1001 | L1 Voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1002 | L1 Current | RO | U16 | 1 | 0.01 | A
Real Time Data | 0x1003 | L1 Power | RO | S32 | 2 | 0.1 | W
Real Time Data | 0x1005 | L1 Frequency | RO | U16 | 1 | 0.01 | Hz
Real Time Data | 0x1006 | L2 Voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1007 | L2 Current | RO | U16 | 1 | 0.01 | A
Real Time Data | 0x1008 | L2 Power | RO | S32 | 2 | 0.1 | W
Real Time Data | 0x100A | L2 Frequency | RO | U16 | 1 | 0.01 | Hz
Real Time Data | 0x100B | L3 Voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x100C | L3 Current | RO | U16 | 1 | 0.01 | A
Real Time Data | 0x100D | L3 Power | RO | S32 | 2 | 0.1 | W
Real Time Data | 0x100F | L3 Frequency | RO | U16 | 1 | 0.01 | Hz
Real Time Data | 0x1010 | MPPT1 Voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1011 | MPPT1 Current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1012 | MPPT1 Power | RO | U32 | 2 | 0.1 | W
Real Time Data | 0x1014 | MPPT2 Voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1015 | MPPT2 Current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1016 | MPPT2 Power | RO | U32 | 2 | 0.1 | W
Real Time Data | 0x1018 | MPPT3 Voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1019 | MPPT3 Current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x101A | MPPT3 Power | RO | U32 | 2 | 0.1 | W
Real Time Data | 0x101C | Inner Temperature | RO | S16 | 1 | 1 | °C
Real Time Data | 0x101D | Inverter Mode | RO | U16 | 1 |  |  | Inverter Mode Table
Real Time Data | 0x101E | Error Code1 | RO | U16 | 1 |  |  | Error Code Table 1
Real Time Data | 0x101F | Error Code2 | RO | U16 | 1 |  |  | Error Code Table 2
Real Time Data | 0x1020 | Error Code3 | RO | U16 | 1 |  |  | Error Code Table 3
Real Time Data | 0x1021 | Total Energy | RO | U32 | 2 |  | kWh
Real Time Data | 0x1023 | Total generation time | RO | U32 | 2 |  | Hour
Real Time Data | 0x1027 | Today Energy | RO | U32 | 2 |  | Wh
Real Time Data | 0x1034 | Fuse open data | RO | U16 | 2 |  |  | Fuse Open Data Table
Real Time Data | 0x1037 | Grid total Active Power | RO | S32 | 2 | 0.1 | W | (L1+L2+L3)
Real Time Data | 0x1039 | Grid total Reactive Power | RO | S32 | 2 | 0.1 | Var | (L1+L2+L3)
Real Time Data | 0x103B | PV Today Peak Power | RO | S32 | 2 | 0.1 | W
Real Time Data | 0x103D | Power Factor | RO | S16 | 1 | 0.001
Real Time Data | 0x103E | MPPT4 Voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x103F | MPPT4 Current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1040 | MPPT4 Power | RO | U32 | 2 | 0.1 | W
Real Time Data | 0X1048 | PV total input power | RO | U32 | 2 | 0.1 | W | (Add all MPPT)
Real Time Data | 0x104C | Decimals of total energy | RO | U16 | 1 |  | Wh | Relate to 0x1021, if total energy is 220.836kWh, then 0x104C is 836Wh
Real Time Data | 0x1080 | MPPT5 Voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1081 | MPPT5 Current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1082 | MPPT5 Power | RO | U32 | 2 | 0.1 | W
Real Time Data | 0x1084 | MPPT6 Voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1085 | MPPT6 Current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1086 | MPPT6 Power | RO | U32 | 2 | 0.1 | W
Real Time Data | 0x1088 | MPPT7 Voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1089 | MPPT7 Current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x108A | MPPT7 Power | RO | U32 | 2 | 0.1 | W
Real Time Data | 0x108C | MPPT8 Voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x108D | MPPT8 Current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x108E | MPPT8 Power | RO | U32 | 2 | 0.1 | W
Real Time Data | 0x1090 | MPPT9 Voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1091 | MPPT9 Current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1092 | MPPT9 Power | RO | U32 | 2 | 0.1 | W
Real Time Data | 0x120C | External fan speed duty percentage | RO | U16 | 1 | 1 | %
Real Time Data | 0x1210 | DER-AVM digital meter connect status | RO | U16 | 1 |  |  | 0: disconnected 1: connected
Real Time Data | 0x1220 | L1-N phase voltage (AC) | RO | U16 | 1 | 0.1 | V | L1-N inverter voltage
Real Time Data | 0x1221 | L2-N phase voltage (AC) | RO | U16 | 1 | 0.1 | V | L2-N inverter voltage
Real Time Data | 0x1222 | L3-N phase voltage (AC) | RO | U16 | 1 | 0.1 | V | L3-N inverter voltage
Real Time Data | 0x1223 | L1-L2 phase voltage (AC) | RO | U16 | 1 | 0.1 | V | L1-L2 inverter voltage
Real Time Data | 0x1224 | L2-L3 phase voltage (AC) | RO | U16 | 1 | 0.1 | V | L2-L3 inverter voltage
Real Time Data | 0x1225 | L3-L1 phase voltage (AC) | RO | U16 | 1 | 0.1 | V | L3-L1 inverter voltage
Real Time Data | 0x1226 | Q (Reference Output reactive power) | RO | S16 | 1 | 0.1 | kVAR
Real Time Data | 0x1300 | L1 watt of grid | RO | S32 | 2 | 0.1 | W | +: Grid to inverter -: Inverter to grid
Real Time Data | 0x1302 | L2 watt of grid | RO | S32 | 2 | 0.1 | W | +: Grid to inverter -: Inverter to grid
Real Time Data | 0x1304 | L3 watt of grid | RO | S32 | 2 | 0.1 | W | +: Grid to inverter
Real Time Data | 0x1306 | Accumulated energy of import | RO | U32 | 2 | 10 | Wh | Grid to inverter
Real Time Data | 0x1308 | Accumulated energy of export | RO | U32 | 2 | 10 | Wh | Inverter to grid
Real Time Data | 0x130A | L1 watt of load | RO | U32 | 2 | 0.1 | W
Real Time Data | 0x130C | L2 watt of load | RO | U32 | 2 | 0.1 | W
Real Time Data | 0x130E | L3 watt of load | RO | U32 | 2 | 0.1 | W
Real Time Data | 0x1310 | Accumulated energy of load | RO | U32 | 2 | 10 | Wh
Real Time Data | 0x131A | L1-N phase voltage of grid | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x131B | L2-N phase voltage of grid | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x131C | L3-N phase voltage of grid | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x131D | L1 current of grid | RO | S32 | 2 | 0.01 | A | +: Grid to inverter -: Inverter to grid
Real Time Data | 0x131F | L2 current of grid | RO | S32 | 2 | 0.01 | A | +: Grid to inverter -: Inverter to grid
Real Time Data | 0x1321 | L3 current of grid | RO | S32 | 2 | 0.01 | A | +: Grid to inverter -: Inverter to grid
Real Time Data | 0x1323 | L1-N phase voltage of load | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1324 | L2-N phase voltage of load | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1325 | L3-N phase voltage of load | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1326 | L1 current of load | RO | S32 | 2 | 0.01 | A
Real Time Data | 0x1328 | L2 current of load | RO | S32 | 2 | 0.01 | A
Real Time Data | 0x132A | L3 current of load | RO | S32 | 2 | 0.01 | A
Real Time Data | 0x1332 | Today import Energy | RO | U32 | 2 | 10 | Wh
Real Time Data | 0x1334 | Today export Energy | RO | U32 | 2 | 10 | Wh
Real Time Data | 0x1336 | Today load Energy | RO | U32 | 2 | 10 | Wh
Real Time Data | 0x1338 | Frequency of grid | RO | U16 | 1 | 0.01 | Hz
Real Time Data | 0x1050 | String1 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1051 | String1 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1052 | String2 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1053 | String2 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1054 | String3 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1055 | String3 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1056 | String4 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1057 | String4 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1058 | String5 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1059 | String5 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x105A | String6 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x105B | String6 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x105C | String7 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x105D | String7 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x105E | String8 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x105F | String8 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1060 | String9 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1061 | String9 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1062 | String10 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1063 | String10 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1064 | String11 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1065 | String11 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1066 | String12 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1067 | String12 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1068 | String13 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1069 | String13 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x106A | String14 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x106B | String14 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x106C | String15 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x106D | String15 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x106E | String16 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x106F | String16 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1070 | String17 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1071 | String17 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1072 | String18 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1073 | String18 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1074 | String19 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1075 | String19 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1076 | String20 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1077 | String20 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x1078 | String21 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x1079 | String21 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x107A | String22 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x107B | String22 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x107C | String23 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x107D | String23 input current | RO | S16 | 1 | 0.01 | A
Real Time Data | 0x107E | String24 input voltage | RO | U16 | 1 | 0.1 | V
Real Time Data | 0x107F | String24 input current | RO | S16 | 1 | 0.01 | A
History Log | 0xB600 | history log 0 | RO | U16 | 3
History Log | 0xB77D | history log 127 | RO | U16 | 3
I-V Curve | 0x8000 | Tracker 1 voltage | RO | U16 | 64 | 0.1 | V
I-V Curve | 0x8040 | String 1-1 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8080 | String 1-2 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x80C0 | String 1-3 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8100 | String 1-4 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8140 | Tracker 2 voltage | RO | U16 | 64 | 0.1 | V
I-V Curve | 0x8180 | String 2-1 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x81C0 | String 2-2 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8200 | String 2-3 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8240 | String 2-4 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8280 | Tracker 3 voltage | RO | U16 | 64 | 0.1 | V
I-V Curve | 0x82C0 | String 3-1 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8300 | String 3-2 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8340 | String 3-3 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8380 | String 3-4 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x83C0 | Tracker 4 voltage | RO | U16 | 64 | 0.1 | V
I-V Curve | 0x8400 | String 4-1 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8440 | String 4-2 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8480 | String 4-3 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x84C0 | String 4-4 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8500 | Tracker 5 voltage | RO | U16 | 64 | 0.1 | V
I-V Curve | 0x8540 | String 5-1 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8580 | String 5-2 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x85C0 | String 5-3 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8600 | String 5-4 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8640 | Tracker 6 voltage | RO | U16 | 64 | 0.1 | V
I-V Curve | 0x8680 | String 6-1 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x86C0 | String 6-2 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8700 | String 6-3 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8740 | String 6-4 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8780 | Tracker 7 voltage | RO | U16 | 64 | 0.1 | V
I-V Curve | 0x87C0 | String 7-1 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8800 | String 7-2 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8840 | String 7-3 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8880 | String 7-4 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x88C0 | Tracker 8 voltage | RO | U16 | 64 | 0.1 | V
I-V Curve | 0x8900 | String 8-1 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8940 | String 8-2 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8980 | String 8-3 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x89C0 | String 8-4 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8A00 | Tracker 9 voltage | RO | U16 | 64 | 0.1 | V
I-V Curve | 0x8A40 | String 9-1 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8A80 | String 9-2 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8AC0 | String 9-3 current | RO | S16 | 64 | 0.01 | A
I-V Curve | 0x8B00 | String 9-4 current | RO | S16 | 64 | 0.01 | A
DEA-AVM Real | 0x03E8 | L1 Current | RO | S32 | 2 | 0.1 | A
DEA-AVM Real | 0x03EA | L2 Current | RO | S32 | 2 | 0.1 | A
DEA-AVM Real | 0x03EC | L3 Current | RO | S32 | 2 | 0.1 | A
DEA-AVM Real | 0x03EE | L1 Voltage | RO | S32 | 2 | 0.1 | V
DEA-AVM Real | 0x03F0 | L2 Voltage | RO | S32 | 2 | 0.1 | V
DEA-AVM Real | 0x03F2 | L3 Voltage | RO | S32 | 2 | 0.1 | V
DEA-AVM Real | 0x03F4 | Grid total Active Power | RO | S32 | 2 | 0.1 | kW | (L1+L2+L3)
DEA-AVM Real | 0x03F6 | Grid total Reactive Power | RO | S32 | 2 |  | Var | (L1+L2+L3)
DEA-AVM Real | 0x03F8 | Power Factor | RO | S32 | 2 | 0.001
DEA-AVM Real | 0x03FA | Frequency | RO | S32 | 2 | 0.1 | Hz
DEA-AVM Real | 0x03FC | Status Flag 1 | RO | S32 | 2 |  |  | Additional description
Parameters | 0x1211 | DER-AVM mode | RW | U16 | 1 |  |  | 0: self control 1: DER-AVM control
Parameters | 0x1240 | RS485-2 Modbus address | RW | U16 | 1 |  |  | [1, 255]
Parameters | 0x1241 | RS485-2 UART baud rate | RW | U16 | 1 |  |  | [3, 6] 3: 9600 4: 14400 5: 19200 6: 38400
Parameters | 0x1242 | RS485-2 terminal resistance control | RW | U16 | 1 |  |  | [0, 1] 0: open, 1: close
Parameters | 0x1243 | RS485-3 Modbus address | RW | U16 | 1 |  |  | [1, 255]
Parameters | 0x1244 | RS485-3 UART baud rate | RW | U16 | 1 |  |  | [3, 6] 3: 9600 4: 14400 5: 19200 6: 38400
Parameters | 0x1245 | RS485-3 terminal resistance control | RW | U16 | 1 |  |  | [0, 1] 0: open, 1: close
Parameters | 0x1A44 | Nominal voltage | RW | U16 | 1 | 0.1 | V
Parameters | 0x3000 | Date：Year | RW | U16 | 1 |  |  | [2000, 2099]
Parameters | 0x3001 | Date：Month + Day | RW | U16 | 1 |  |  | [1, 12] High Byte=Month
Parameters | 0x3002 | Date：Hour + Minute | RW | U16 | 1 |  |  | [0, 23] High Byte =Hour
Parameters | 0x3003 | Date：Second + 0 | RW | U16 | 1 |  |  | [0, 59] High Byte =Second
Parameters | 0x3005 | Power derating percent by Modbus | RW | U16 | 1 |  |  | [0, 110] Dynamic active power regulation.
Parameters | 0x303E | RS485-1 Modbus Address | RW | U16 | 1 |  |  | [1, 247] Default 1
Parameters | 0x304C | RS485-1 baud rate | RW | U16 | 1 |  |  | [0, 6] 0: undefined 3: 9600 4: 14400 5: 19200 6: 38400
Parameters | 0x3060 | WIFI STA SSID | RW | string | 16 |  | ASCII
Parameters | 0x3070 | WIFI STA password | RW | string | 16 |  | ASCII
Parameters | 0x30B0 | Digital meter Modbus address | RW | U16 | 1 |  |  | [1, 255] Default 1
Parameters | 0x30B1 | Digital meter Type | RW | U16 | 1 |  |  | [0, 10] 0: Unknown 1: Gavazzi / EM340DINAV23XS1X 2: CHINT/DTSU666 3: Reserved 4: Lovato/DMG210 5: Reserved 6: Gavazzi/ET112 7: Reserved 8: CHINT/DDSU666 9: Gavazzi / EM530DINAV53XS1X 10: Gavazzi / EM540DINAV53XS1X
Parameters | 0x30B2 | Power flow direction | RW | U16 | 1 |  |  | [0, 1] 0: Grid to inverter 1: Inverter to grid
Parameters | 0x30B3 | Power limit function | RW | U16 | 1 |  |  | [0, 3] 0: Disable 1: Power limit by external device 2: Power limit by PVI external CT 3: Power limit by digital meter
Parameters | 0x30B4 | Power limit CT ratio | RW | U16 | 1 |  |  | [0, 8] 0: Unknown 1: 1000 : 1 2: 2000 : 1 3: 2500 : 1 4: 3000 : 1 5: 4000 : 1 6: 5000 : 1 7: 6000 : 1 8: 10000 : 1
Parameters | 0x30B5 | Meter location | RW | U16 | 1 |  |  | [0, 1] 0: CT on Grid (Meter on Grid) 1: CT on Load (Meter on Load)
Parameters | 0x30B9 | Maximum feed in grid power | RW | U32 | 2 |  | W | [0, Pnom] Pnom : nominal power
Parameters | 0x5000 | First connect start time | RW | U16 | 1 |  | s | [10, 600]
Parameters | 0x5001 | Reconnect time | RW | U16 | 1 |  | s | [10, 900]
Parameters | 0x5002 | Grid frequency high loss level 1 limit | RW | U16 | 1 | 0.01 | Hz | 50Hz: [5001, 5500] 60Hz: [6001, 6500]
Parameters | 0x5003 | Grid frequency low loss level 1 limit | RW | U16 | 1 | 0.01 | Hz | 50Hz: [4500, 4999] 60Hz: [5500, 5999]
Parameters | 0x5004 | Grid voltage high loss level 1 limit | RW | U16 | 1 | 0.1 | V | [1, 1.5] * nominal voltage
Parameters | 0x5005 | Grid voltage low loss level 1 limit | RW | U16 | 1 | 0.1 | V | [0.1, 1] * nominal voltage
Parameters | 0x5006 | Grid frequency high loss level 1 trip time | RW | U16 | 1 | 1 | ms | [0, 65535]
Parameters | 0x5007 | Grid frequency low loss level 1 trip time | RW | U16 | 1 | 1 | ms | [0, 65535] For CN (NB/T 32004) regulation code (0x5101=0x0E), the unit is 10ms. Other regulation codes use 1ms.
Parameters | 0x5008 | Grid voltage high loss level 1 trip time | RW | U16 | 1 | 1 | ms | [0, 65535] For CN (NB/T 32004) regulation code (0x5101=0x0E), the unit is 10ms. Other regulation codes use 1ms.
Parameters | 0x5009 | Grid voltage low loss level 1 trip time | RW | U16 | 1 | 1 | ms | [0, 65535] For CN (NB/T 32004) regulation code (0x5101=0x0E), the unit is 10ms. Other regulation codes use 1ms.
Parameters | 0x500A | Grid frequency high loss level 2 limit | RW | U16 | 1 | 0.01 | Hz | 50Hz: [5001, 5500] 60Hz: [6001, 6500]
Parameters | 0x500B | Grid frequency low loss level 2 limit | RW | U16 | 1 | 0.01 | Hz | 50Hz: [4500, 4999] 60Hz: [5500, 5999]
Parameters | 0x500C | Grid voltage high loss level 2 limit | RW | U16 | 1 | 0.1 | V | [1, 1.5] * nominal voltage
Parameters | 0x500D | Grid voltage low loss level 2 limit | RW | U16 | 1 | 0.1 | V | [0.1, 1] * nominal voltage
Parameters | 0x500E | Grid frequency high loss level 2 trip time | RW | U16 | 1 | 1 | ms | [0, 65535] For CN (NB/T 32004) regulation code (0x5101=0x0E), the unit is 10ms. Other regulation codes use 1ms.
Parameters | 0x500F | Grid frequency low loss level 2 trip time | RW | U16 | 1 | 1 | ms | [0, 65535] For CN (NB/T 32004) regulation code (0x5101=0x0E), the unit is 10ms. Other regulation codes use 1ms.
Parameters | 0x5010 | Grid voltage high loss level 2 trip time | RW | U16 | 1 | 1 | ms | [0, 65535] For CN (NB/T 32004) regulation code (0x5101=0x0E), the unit is 10ms. Other regulation codes use 1ms.
Parameters | 0x5011 | Grid voltage low loss level 2 trip time | RW | U16 | 1 | 1 | ms | [0, 65535] For CN (NB/T 32004) regulation code (0x5101=0x0E), the unit is 10ms. Other regulation codes use 1ms.
Parameters | 0x5012 | Grid Frequency High Level 1 back | RW | U16 | 1 | 0.01 | Hz | 50Hz: [5001, 5500] 60Hz: [6001, 6500]
Parameters | 0x5013 | Grid Frequency Low Level 1 back | RW | U16 | 1 | 0.01 | Hz | 50Hz: [5001, 5500] 60Hz: [6001, 6500]
Parameters | 0x5018 | 10 min average sustained voltage | RW | U16 | 1 | 0.1 | V | [1, 1.5] * nominal voltage
Parameters | 0x5019 | Reconnect soft output power percent | RW | U16 | 1 |  | %/min | [1,100]
Parameters | 0x501A | Over frequency power reduction droop | RW | U16 | 1 | 0.1 | %/Hz | [20,120]
Parameters | 0x501B | Insulation resistance active limit | RW | U16 | 1 | 1 | KΩ | [10,5000]
Parameters | 0x501E | Grid over voltage de-rating point | RW | U16 | 1 | 0.1 | V | [1, 1.5] * nominal voltage
Parameters | 0x501F | Grid frequency high Level 1 trip time (High word) | RW | U16 | 1 |  | ms | [0,15]
Parameters | 0x5020 | Grid frequency low Level 1 trip time (High word) | RW | U16 | 1 |  | ms | [0,15]
Parameters | 0x5021 | Grid over frequency de-rating start point | RW | U16 | 1 | 0.01 | Hz | 50Hz: [5001, 5500] 60Hz: [6001, 6500]
Parameters | 0x5022 | Grid over frequency de-rating end point | RW | U16 | 1 | 0.01 | Hz | 50Hz: [5001, 5500] 60Hz: [6001, 6500]
Parameters | 0x5025 | Grid Voltage High Level 1 trip time (High word) | RW | U16 | 1 |  | ms | [0,9]
Parameters | 0x5026 | Grid Voltage Low Level 1 trip time (High word) | RW | U16 | 1 |  | ms | [0,9]
Parameters | 0x5027 | Grid Voltage High Level 1 back | RW | U16 | 1 | 0.1 | V | [nominal voltage + 1, nominal voltage * 1.5]
Parameters | 0x5028 | Grid Voltage Low Level 1 back | RW | U16 | 1 | 0.1 | V | [0, nominal voltage - 1]
Parameters | 0x5029 | First connect soft start output power percent | RW | U16 | 1 |  | % | [1,100]
Parameters | 0x5030 | Output reactive power mode | RW | U16 | 1 |  |  | [0,9]
Parameters | 0x5031 | Power factor setting | RW | S16 | 1 | 0.001 |  | [-1000, -800], [800, 1000]
Parameters | 0x5033 | Reactive control response time | RW | U16 | 1 |  | s | [0,120]
Parameters | 0x503C | Q(U) curve node1 percent(U/Un) | RW | U16 | 1 |  | % | [80,120]
Parameters | 0x503D | Q(U) curve node2 percent(U/Un) | RW | U16 | 1 |  | % | [80,120]
Parameters | 0x503E | Q(U) curve node3 percent(U/Un) | RW | U16 | 1 |  | % | [80,120]
Parameters | 0x503F | Q(U) curve node4 percent(U/Un) | RW | U16 | 1 |  | % | [80,120]
Parameters | 0x5040 | Q(U) curve node1 value setting (Q/S) | RW | S16 | 1 | 0.1 | % | [-1100,1100]
Parameters | 0x5041 | Q(U) curve node2 value setting (Q/S) | RW | S16 | 1 | 0.1 | % | [-1100,1100]
Parameters | 0x5042 | Q(U) curve node3 value setting (Q/S) | RW | S16 | 1 | 0.1 | % | [-1100,1100]
Parameters | 0x5043 | Q(U) curve node4 value setting (Q/S) | RW | S16 | 1 | 0.1 | % | [-1100,1100]
Parameters | 0x504B | Volt-Watt node1 voltage for output power derating | RW | U16 | 1 | 0.1 | V | [0.8, 1.5] * nominal voltage
Parameters | 0x504C | Volt-Watt node2 voltage for output power derating | RW | U16 | 1 | 0.1 | V | [0.8, 1.5] * nominal voltage
Parameters | 0x504F | Volt-Watt node1 output power percent | RW | U16 | 1 |  | % | [0,110]
Parameters | 0x5050 | Volt-Watt node2 output power percent | RW | U16 | 1 |  | % | [0,110]
Parameters | 0x505A | Q(P) curve node 1 percentage setting (P/Pn) | RW | U16 | 1 |  | % | [0,100]
Parameters | 0x505B | Q(P) curve node 2 percentage setting (P/Pn) | RW | U16 | 1 |  | % | [0,100]
Parameters | 0x505C | Q(P) curve node 3 percentage setting (P/Pn) | RW | U16 | 1 |  | % | [0,100]
Parameters | 0x505D | Q(P) curve node 4 percentage setting (P/Pn) | RW | U16 | 1 |  | % | [0,100]
Parameters | 0x505E | Q(P) curve node 1 value setting (Q/Pn) | RW | S16 | 1 | 0.1 | % | [-600,600]
Parameters | 0x505F | Q(P) curve node 2 value setting (Q/Pn) | RW | S16 | 1 | 0.1 | % | [-600,600]
Parameters | 0x5060 | Q(P) curve node 3 value setting (Q/Pn) | RW | S16 | 1 | 0.1 | % | [-600,600]
Parameters | 0x5061 | Q(P) curve node 4 value setting (Q/Pn) | RW | S16 | 1 | 0.1 | % | [-600,600]
Parameters | 0x5063 | LVRT Triggering voltage | RW | U16 | 1 | 0.1 | V | [0.1, 0.9] * nominal voltage
Parameters | 0x5064 | HVRT Triggering voltage | RW | U16 | 1 | 0.1 | V | [1.1, 1.5] * nominal voltage
Parameters | 0x5065 | FRT Mode | RW | U16 | 1 |  |  | [0, 1] 0: Zero current mode, 1: full grid support mode
Parameters | 0x5066 | FRT Zero current mode triggering threshold | RW | U16 | 1 |  | % | [5, 150]
Parameters | 0x5067 | FRT grid voltage jump triggering threshold | RW | U16 | 1 |  | % | [5, 150]
Parameters | 0x506C | Grid frequency high Level 2 trip time (High word) | RW | U16 | 1 |  | ms | [0, 15]
Parameters | 0x506D | Grid frequency low Level 2 trip time (High word) | RW | U16 | 1 |  | ms | [0, 15]
Parameters | 0x5070 | Grid frequency high level 3 limit | RW | U16 | 1 | 0.01 | Hz | 50Hz: [5001, 5500] 60Hz: [6001, 6500]
Parameters | 0x5071 | Grid frequency low level 3 limit | RW | U16 | 1 | 0.01 | Hz | 50Hz: [4500, 4999] 60Hz: [5500, 5999]
Parameters | 0x5072 | Grid voltage high level 3 limit | RW | U16 | 1 | 0.1 | V | [1, 1.5] * nominal voltage
Parameters | 0x5073 | Grid voltage low level 3 limit | RW | U16 | 1 | 0.1 | V | [0.1, 1] * nominal voltage
Parameters | 0x5074 | Grid Frequency High Level 3 trip time | RW | U16 | 1 |  | ms | [0, 65535]
Parameters | 0x5075 | Grid Frequency Low Level 3 trip time | RW | U16 | 1 |  | ms | [0, 65535]
Parameters | 0x5076 | Grid Voltage High Level 3 trip time | RW | U16 | 1 |  | ms | [0, 65535]
Parameters | 0x5077 | Grid Voltage Low Level 3 trip time | RW | U16 | 1 |  | ms | [0, 65535]
Parameters | 0x507F | Over frequency derating reference power | RW | U16 | 1 |  |  | [0, 1] 0: base on rating power, 1: base on current power
Parameters | 0x5081 | Grid under frequency rise power start point | RW | U16 | 1 | 0.01 | Hz | 50Hz: [4500, 4999] 60Hz: [5500, 5999]
Parameters | 0x5082 | Grid under frequency rise power stop point | RW | U16 | 1 | 0.01 | Hz | 50Hz: [4500, 4999] 60Hz: [5500, 5999]
Parameters | 0x5083 | Under frequency rise power droop | RW | U16 | 1 | 0.001 |  | [20, 120]
Parameters | 0x5084 | Under frequency rise power reference | RW | U16 | 1 |  |  | [0, 1] 0: base on rating power, 1: base on current power
Parameters | 0x5101 | Regulation code | RW | U16 | 1 |  |  | Regulation Code Table
Parameters | 0x5104 | Derating Watt Percent | RW | U16 | 1 |  | % | [0, 110] Percent of nominal power
Parameters | 0x5106 | Mppt shadow manage | RW | U16 | 1 |  |  | [0, 1] 0: disable, 1: enable
Parameters | 0x5107 | Mppt shadow manage interval time | RW | U16 | 1 |  | s | [30, 7200]
Parameters | 0x510E | Islanding detection | RW | U16 | 1 |  |  | [0, 1] 0: disable, 1: enable
Parameters | 0x5110 | Ground current limit | RW | U16 | 1 |  | mA | [1, S*0.01]
Parameters | 0x5112 | Low voltage through detection | RW | U16 | 1 |  |  | [0, 1] 0: disable, 1: enable Only support for 3 phase model (0x1A48 = 3).
Parameters | 0x5114 | Reactive Power Percent | RW | S16 | 1 |  | % | [-60, 60] Percent of nominal power Do not use for dynamic regulation.
Parameters | 0x5115 | RS485-1 terminal resistance control | RW | U16 | 1 |  |  | [0, 1] 0: open, 1: close Only support for 3 phase model (0x1A48 = 3).
Parameters | 0x5117 | Insulation Resistor Detection | RW | U16 | 1 |  |  | [0, 1] 0: disable, 1: enable
Parameters | 0x5118 | Ground Current Detection | RW | U16 | 1 |  |  | [0, 1] 0: disable, 1: enable
Parameters | 0x511D | Grid high voltage load de-rating function | RW | U16 | 1 |  |  | [0, 1] 0: disable, 1: enable Relation with [0x501E]
Parameters | 0x5121 | Reactive Power Percent | RW | S16 | 1 | 0.01 | % | [-11000, 11000]
Parameters | 0x513D | Fuse open Check Mask | RW | U32 | 2 |  |  | Fuse open Check Mask Table
Parameters | 0x6001 | Inverter control | RW | U16 | 1 |  |  | [0, 1] 0: power on, 1: shut down
Parameters | 0x6006 | EEPROM default | RW | U16 | 1 |  |  | [0, 1] 0: EEPROM setting NOT to default 1: EEPROM setting to default
Parameters | 0x6009 | Clear the EEPROM history energy record | RW | U16 | 1 |  |  | [0, 1] 0: NOT clear the EEPROM history energy record 1: Clear the EEPROM history energy record
Parameters | 0x600D | I-V curve scan | RW | U16 | 1 |  |  | Write: 0x0000: Non-active 0x0001: Active Read: 0x0000: Idle or had been read 0x0001: Running 0x0002: Finished
Parameters | 0x600F | P.F (cosφ) | RW | S16 | 1 | 0.001 |  | [-1000, -800], [800,1000] (+) Positive: over-excited(lag, inductive) (-) Negative: under-excited(lead, capacitive) Dynamic power factor regulation.
Parameters | 0x6010 | Reactive Power Percent | RW | S16 | 1 | 0.01 | % | [0, 65535] (+) Positive: over-excited(lag, inductive) (-) Negative: under-excited(lead, capacitive) Dynamic reactive power regulation.
DER-AVM Set | 0x07D0 | Power factor setting | RW | S16 | 1 | 0.001 |  | [-1000, -800], [800, 1000] Default 1000
DER-AVM Set | 0x07D1 | Action mode | RW | U16 | 1 |  |  | 0: self-control 2: DER-AVM control 5: Q(V)control Default 2
DER-AVM Set | 0x07D2 | Reactive power percent setting | RW | S16 | 1 | 0.1 | % | [-484, 484] Default 0
DER-AVM Set | 0x07D3 | Active power percent setting | RW | U16 | 1 | 0.1 | % | [0, 1100] Default 1000
DER-AVM Set | 0x0834 | Inverter off | RW | U16 | 1 |  |  | 0: Inverter on 1: Inverter off Default 0
DER-AVM Set | 0x0835 | Clear PV insulation warning | RW | U16 | 1 |  |  | 0: Non-active 1: Clear PV insulation abnormal warning

## Alarm
Alarm Group | Address | Bit | Alarm Description (알람 내용) | 정상 상태 | 발생 상태
Error Code 1 | 0x101E | 0 | [Err 16] Inverter over dc-bias current | 0 | 1
Error Code 1 | 0x101E | 1 | [Err 17] Inverter relay abnormal | 0 | 1
Error Code 1 | 0x101E | 2 | [Err 18] Remote off | 0 | 1
Error Code 1 | 0x101E | 3 | [Err 19] Inverter over temperature | 0 | 1
Error Code 1 | 0x101E | 4 | [Err 20] GFCI abnormal | 0 | 1
Error Code 1 | 0x101E | 5 | [Err 21] PV string reverse | 0 | 1
Error Code 1 | 0x101E | 6 | [Err 22] System type error | 0 | 1
Error Code 1 | 0x101E | 7 | [Err 23] Fan abnormal | 0 | 1
Error Code 1 | 0x101E | 8 | [Err 24] Dc-link unbalance or under voltage | 0 | 1
Error Code 1 | 0x101E | 9 | [Err 25] Dc-link over voltage | 0 | 1
Error Code 1 | 0x101E | 10 | [Err 26] Internal communication error | 0 | 1
Error Code 1 | 0x101E | 11 | [Err 27] Software incompatibility | 0 | 1
Error Code 1 | 0x101E | 12 | [Err 28] Internal storage error | 0 | 1
Error Code 1 | 0x101E | 13 | [Err 29] Data inconsistency | 0 | 1
Error Code 1 | 0x101E | 14 | [Err 30] Inverter abnormal | 0 | 1
Error Code 1 | 0x101E | 15 | [Err 31] Boost abnormal | 0 | 1
Error Code 2 | 0x101F | 0 | [Err 0] Grid over voltage | 0 | 1
Error Code 2 | 0x101F | 1 | [Err 1] Grid under voltage | 0 | 1
Error Code 2 | 0x101F | 2 | [Err 2] Grid absent | 0 | 1
Error Code 2 | 0x101F | 3 | [Err 3] Grid over frequency | 0 | 1
Error Code 2 | 0x101F | 4 | [Err 4] Grid under frequency | 0 | 1
Error Code 2 | 0x101F | 5 | [Err 5] PV over voltage | 0 | 1
Error Code 2 | 0x101F | 6 | [Err 6] PV insulation abnormal | 0 | 1
Error Code 2 | 0x101F | 7 | [Err 7] Leakage current abnormal | 0 | 1
Error Code 2 | 0x101F | 8 | [Err 8] Inverter in power limit state | 0 | 1
Error Code 2 | 0x101F | 9 | [Err 9] Internal power supply abnormal | 0 | 1
Error Code 2 | 0x101F | 10 | [Err 10] PV string abnormal | 0 | 1
Error Code 1 | 0x101E | 0 | [Err 16] Inverter over dc-bias current | 0 | 1
Error Code 1 | 0x101E | 1 | [Err 17] Inverter relay abnormal | 0 | 1
Error Code 1 | 0x101E | 2 | [Err 18] Remote off | 0 | 1
Error Code 1 | 0x101E | 3 | [Err 19] Inverter over temperature | 0 | 1
Error Code 1 | 0x101E | 4 | [Err 20] GFCI abnormal | 0 | 1
Error Code 1 | 0x101E | 5 | [Err 21] PV string reverse | 0 | 1
Error Code 1 | 0x101E | 6 | [Err 22] System type error | 0 | 1
Error Code 1 | 0x101E | 7 | [Err 23] Fan abnormal | 0 | 1
Error Code 1 | 0x101E | 8 | [Err 24] Dc-link unbalance or under voltage | 0 | 1
Error Code 1 | 0x101E | 9 | [Err 25] Dc-link over voltage | 0 | 1
Error Code 1 | 0x101E | 10 | [Err 26] Internal communication error | 0 | 1
Error Code 1 | 0x101E | 11 | [Err 27] Software incompatibility | 0 | 1
Error Code 1 | 0x101E | 12 | [Err 28] Internal storage error | 0 | 1
Error Code 1 | 0x101E | 13 | [Err 29] Data inconsistency | 0 | 1
Error Code 1 | 0x101E | 14 | [Err 30] Inverter abnormal | 0 | 1
Error Code 1 | 0x101E | 15 | [Err 31] Boost abnormal | 0 | 1
Error Code 2 | 0x101F | 0 | [Err 0] Grid over voltage | 0 | 1
Error Code 2 | 0x101F | 1 | [Err 1] Grid under voltage | 0 | 1
Error Code 2 | 0x101F | 2 | [Err 2] Grid absent | 0 | 1
Error Code 2 | 0x101F | 3 | [Err 3] Grid over frequency | 0 | 1
Error Code 2 | 0x101F | 4 | [Err 4] Grid under frequency | 0 | 1
Error Code 2 | 0x101F | 5 | [Err 5] PV over voltage | 0 | 1
Error Code 2 | 0x101F | 6 | [Err 6] PV insulation abnormal | 0 | 1
Error Code 2 | 0x101F | 7 | [Err 7] Leakage current abnormal | 0 | 1
Error Code 2 | 0x101F | 8 | [Err 8] Inverter in power limit state | 0 | 1
Error Code 2 | 0x101F | 9 | [Err 9] Internal power supply abnormal | 0 | 1
Error Code 2 | 0x101F | 10 | [Err 10] PV string abnormal | 0 | 1
Error Code 2 | 0x101F | 11 | [Err 11] PV under voltage | 0 | 1
Error Code 2 | 0x101F | 12 | [Err 12] PV irradiation weak | 0 | 1
Error Code 2 | 0x101F | 13 | [Err 13] Grid abnormal | 0 | 1
Error Code 2 | 0x101F | 14 | [Err 14] Arc fault detection | 0 | 1
Error Code 2 | 0x101F | 15 | [Err 15] AC moving average voltage high | 0 | 1
Error Code 3 | 0x1020 | 0 | [Err 32] Reserved | 0 | 1
Error Code 3 | 0x1020 | 1 | [Err 33] Logger/E-Display EEPROM fail | 0 | 1
Error Code 3 | 0x1020 | 2 | [Err 34] Reserved | 0 | 1
Error Code 3 | 0x1020 | 3 | [Err 35] Single tracker detect warning (PID device abnormal) | 0 | 1
Error Code 3 | 0x1020 | 4 | [Err 36] AFCI lost | 0 | 1
Error Code 3 | 0x1020 | 5 | [Err 37] Data logger lost | 0 | 1
Error Code 3 | 0x1020 | 6 | [Err 38] Meter lost | 0 | 1
Error Code 3 | 0x1020 | 7 | [Err 39] Inverter lost | 0 | 1
Error Code 3 | 0x1020 | 8 | [Err 40] Grid N abnormal | 0 | 1
Error Code 3 | 0x1020 | 9 | [Err 41] Surge Protection Devices (SPD) defective | 0 | 1
Error Code 3 | 0x1020 | 10 | [Err 42] Parallel ID warning | 0 | 1
Error Code 3 | 0x1020 | 11 | [Err 43] Parallel SYN signal warning | 0 | 1
Error Code 3 | 0x1020 | 12 | [Err 44] Parallel BAT abnormal | 0 | 1
Error Code 3 | 0x1020 | 13 | [Err 45] Parallel GRID abnormal | 0 | 1
Error Code 3 | 0x1020 | 14 | [Err 46] Generator voltage abnormal | 0 | 1
Error Code 3 | 0x1020 | 15 | [Err 47] Reserved | 0 | 1
REMS Error | Payload | 0 | Inverter action state, [0,1] | inverter running | inverter stop
REMS Error | Payload | 1 | Solar battery over voltage, [0,1] | normal | over voltage
REMS Error | Payload | 2 | Solar battery under voltage, [0,1] | normal | under voltage
REMS Error | Payload | 3 | Solar battery over current, [0,1] | normal | over current
REMS Error | Payload | 4 | Inverter IGBT error, [0,1] | normal | error
REMS Error | Payload | 5 | Inverter over temperature, [0,1] | normal | over temperature
REMS Error | Payload | 6 | Grid over voltage, [0,1] | normal | over voltage
REMS Error | Payload | 7 | Grid under voltage, [0,1] | normal | under voltage
REMS Error | Payload | 8 | Grid over current, [0,1] | normal | over current
REMS Error | Payload | 9 | Grid over frequency, [0,1] | normal | over frequency
REMS Error | Payload | 10 | Grid under frequency, [0,1] | normal | under frequency
REMS Error | Payload | 11 | Self control(outage), [0,1] | normal | outage
REMS Error | Payload | 12 | Leakage current abnormal, [0,1] | normal | abnormal

## Command
Modbus Protocol Command
Function Code List
Index | Function Code | Description
1 | 0x03 | Read register address
2 | 0x06 | Write a single register address
3 | 0x10 | Write multiple register address
4 | 0x7E | REMS read register address
Read Register (0x03) - Host query command format
Parameter | Length (Byte) | Description
Slave address | 1 | 1~247
Function code | 1 | 0x03
Register start address | 2 | 0x0000~0xFFFF
Register number | 2 | 1~124
CRC code | 2
Read Register (0x03) - Slave normal respond
Parameter | Length (Byte) | Description
Slave address | 1 | 1~247
Function code | 1 | 0x03
Byte number | 1 | Register Number*2
Register value | 2 ~ 248
CRC code | 2
Read Register (0x03) - Slave abnormal respond
Parameter | Length (Byte) | Description
Slave address | 1 | 1~247
Function code | 1 | 0x83
Illegal code | 1 | Refer “Illegal CodeTable”
CRC code | 2
Example | Hex string
Host query example | 01 03 10 01 00 01 D1 0A
Slave normal respond | 01 03 02 08 FC BF C5
Slave abnormal respond | 01 83 02 C0 F1
Write a single Register (0x06) - Host query command format
Parameter | Length (Byte) | Description
Slave address | 1 | 1~247
Function code | 1 | 0x06
Register address | 2 | 0x0000~0xFFFF
Register value | 2 | 0x0000~0xFFFF
CRC code | 2
Write a single Register (0x06) - Slave normal respond
Parameter | Length (Byte) | Description
Slave address | 1 | 1~247
Function code | 1 | 0x06
Register address | 2 | 0x0000~0xFFFF
Register value | 2 | 0x0000~0xFFFF
CRC code | 2
Write a single Register (0x06) - Slave abnormal respond
Parameter | Length (Byte) | Description
Slave address | 1 | 1~247
Function code | 1 | 0x86
Illegal code | 1 | Refer “Illegal CodeTable”
CRC code | 2
Example | Hex string
Host query example | 01 06 51 01 00 01 09 36
Slave normal respond | 01 06 51 01 00 01 09 36
Slave abnormal respond | 01 86 04 43 A3
Write multiple Registers (0x10) - Host query command format
Parameter | Length (Byte) | Description
Slave address | 1 | 1~247
Function code | 1 | 0x10
Register start address | 2 | 0x0000~0xFFFF
Register number | 2 | 1~122
Byte number | 1 | Register Number * 2
Register value | 2 ~ 244
CRC code | 2
Write multiple Registers (0x10) - Slave normal respond
Parameter | Length (Byte) | Description
Slave address | 1 | 1~247
Function code | 1 | 0x10
Register start address | 2 | 0x0000~0xFFFF
Register number | 2 | 1~122
CRC code | 2
Write multiple Registers (0x10) - Slave abnormal respond
Parameter | Length (Byte) | Description
Slave address | 1 | 1~247
Function code | 1 | 0x90
Illegal code | 1 | Refer “Illegal CodeTable”
CRC code | 2
Example | Hex string
Host query example | 01 10 30 00 00 04 08 07 E1 01 01 00 00 00 00 7B 73
Slave normal respond | 01 10 30 00 00 04 CE CA
Slave abnormal respond | 01 90 02 CD C1
REMS read register address (0x7E) - Slave normal respond format
Parameter | Length (Byte) | Description
Function code | 1 | 0x7E
Slave address | 1 | 1~247
Command | 1 | 0x08
Byte number | 2 | 0x26
Register value | 38
CRC code | 2
Example | Hex string
Host query example | 7E 01 07 51 8A
Slave normal respond | 7E 01 08 00 26 00 6E 00 0A 00 00 22 DE 01 9B 01 97 01 9A 00 0C 00 0C 00 0C 00 00 1F A8 03 E1 01 F4 00 00 00 00 48 2F C8 38 00 00 56 6C