## 1_INFO
Stage 1 — 레지스터맵 추출 (MAPPING_RULES_V2)
제조사 | Solarize
프로토콜 버전
설비 타입 | inverter
MPPT | 9
String | 24
String 모니터링 | Yes
IV Scan | Yes
IV Data Points | 64
IV Trackers | 9
원본 파일 | Solarize-PV_Modbus_Protocol-Korea-V1.2.4.pdf
추출 일시 | 2026-04-06 13:21
H01 매칭 | 60/60
DER 매칭 | 33/33
추출 레지스터 | 315
REVIEW | 0
INFO 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | DAILY_ENERGY | 0x1027 | 03 | U32 | Wh | RO | daily_energy | Today Energy
2 | L1_N_PHASE_VOLTAGE_OF_GRID | 0x131A | 03 | U16 | V 0.1 | RO |  | L1-N phase voltage of grid
3 | L2_N_PHASE_VOLTAGE_OF_GRID | 0x131B | 03 | U16 | V 0.1 | RO |  | L2-N phase voltage of grid
4 | L3_N_PHASE_VOLTAGE_OF_GRID | 0x131C | 03 | U16 | V 0.1 | RO |  | L3-N phase voltage of grid
5 | L1_N_PHASE_VOLTAGE_OF_LOAD | 0x1323 | 03 | U16 | V 0.1 | RO |  | L1-N phase voltage of load
6 | L2_N_PHASE_VOLTAGE_OF_LOAD | 0x1324 | 03 | U16 | V 0.1 | RO |  | L2-N phase voltage of load
7 | L3_N_PHASE_VOLTAGE_OF_LOAD | 0x1325 | 03 | U16 | V 0.1 | RO |  | L3-N phase voltage of load
8 | DEVICE_MODEL_NAME | 0x1A00 | 03 | STRINGING |  | RO |  | Device Model name ¦ Ex.：PV 30KTL
9 | DEVICE_SERIAL_NUMBER | 0x1A10 | 03 | STRINGING |  | RO |  | Device Serial number ¦ Ex.：1234-123456789
10 | MASTER_FIRMWARE_VERSION | 0x1A1C | 03 | STRINGING |  | RO |  | Master firmware version ¦ Ex.：123456
11 | SLAVE_FIRMWARE_VERSION | 0x1A26 | 03 | STRINGING |  | RO |  | Slave firmware version ¦ Ex.：123456
12 | NOMINAL_VOLTAGE | 0x1A44 | 03 | U16 |  | RO |  | Nominal Voltage ¦ Ex.：2200 = 220V
13 | NOMINAL_FREQUENCY | 0x1A45 | 03 | U16 |  | RO |  | Nominal Frequency ¦ Ex.：5000 = 50Hz
14 | NOMINAL_ACTIVE_POWER_LOW_WORD | 0x1A46 | 03 | U16 | W 1 | RO |  | Nominal Active Power(Low word) ¦ Ex.：1500 = 1500W
15 | GRID_PHASE_NUMBER | 0x1A48 | 03 | U16 |  | RO |  | Grid Phase Number ¦ 1=single phase2=split phase3=three phases
16 | NOMINAL_ACTIVE_POWER_HIGH_WORD | 0x1A4E | 03 | U16 | W 1 | RO |  | Nominal Active Power(High word) ¦ Ex.：1 = (1*65536)W
17 | EMS_FIRMWARE_VERSION | 0x1A60 | 03 | STRINGING |  | RO |  | EMS Firmware Version ¦ Ex.：123456
18 | LCD_FIRMWARE_VERSION | 0x1A8E | 03 | STRINGING |  | RO |  | LCD firmware version ¦ Ex.：123456
STATUS 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | INVERTER_MODE | 0x101D | 03 | U16 |  | RO | inverter_status | Inverter Mode ¦ Inverter Mode Table
ALARM 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | GFCI_ABNORMAL | 0x0004 | 03 | U16 |  | RO | r_voltage | GFCI abnormal
2 | PV_STRING_REVERSE | 0x0005 | 03 | STRINGING |  | RO | s_voltage | PV string reverse
3 | ERROR_CODE1 | 0x101E | 03 | U16 |  | RO |  | Error Code1 ¦ Error Code Table 1
4 | ERROR_CODE2 | 0x101F | 03 | U16 |  | RO |  | Error Code2 ¦ Error Code Table 2
5 | ERROR_CODE3 | 0x1020 | 03 | U16 |  | RO |  | Error Code3 ¦ Error Code Table 3

## 2_H01
H01 모니터링 매칭 — 60/60
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER | S32 | W | 0.1 | DER-AVM 고정 주소 사용
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR | S32 |  | 0.1 | DER-AVM 고정 주소 사용
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY | S32 | Hz | 0.1 | DER-AVM 고정 주소 사용
10 | pv_voltage | HANDLER | O | - | - | U16 | V |  | handler 계산: average(MPPT_N_voltage for N if voltage > 100V)
11 | pv_current | HANDLER | O | - | - | U16 | A |  | handler 계산: 1순위: sum(STRING_N_current), 2순위: sum(MPPT_N_current)
12 | pv_power | PDF | O | 0x1048 | PV_POWER | U32 | W | 0.1
13 | cumulative_energy | PDF | O | 0x1021 | CUMULATIVE_ENERGY | U32 | kWh |  | kWh→Wh (*1000)
14 | cumulative_energy_low | PDF | O | 0x104C | CUMULATIVE_ENERGY | U16
15 | status | PDF | O | 0x101D | INVERTER_MODE | U16 |  |  | 6=PV6 fuse open d, 7=PV7 fuse open d, 8=PV8 fuse open d
16 | alarm1 | PDF | O | 0x101E | ERROR_CODE1 | U16 |  |  | 0=Inverter over d, 1=Inverter relay , 2=Remote off, 3=Inverter over t, 4=GFCI abnormal, 5=PV string rever... (+10)
17 | alarm2 | PDF | O | 0x101F | ERROR_CODE2 | U16 |  |  | 136=String 1-2 curr, 137=String 1-3 curr, 138=String 1-4 curr, 139=Tracker 2 volta, 140=String 2-1 curr, 141=String 2-2 curr... (+33)
18 | alarm3 | PDF | O | 0x1020 | ERROR_CODE3 | U16
19 | mppt1_voltage | PDF | O | 0x1010 | PV_VOLTAGE | U16 | V | 0.1
20 | mppt1_current | PDF | O | 0x1011 | MPPT1_CURRENT | S16 | A | 0.01
21 | mppt2_voltage | PDF | O | 0x1014 | MPPT2_VOLTAGE | U16 | V | 0.1
22 | mppt2_current | PDF | O | 0x1015 | MPPT2_CURRENT | S16 | A | 0.01
23 | mppt3_voltage | PDF | O | 0x1018 | MPPT3_VOLTAGE | U16 | V | 0.1
24 | mppt3_current | PDF | O | 0x1019 | MPPT3_CURRENT | S16 | A | 0.01
25 | mppt4_voltage | PDF | O | 0x103E | MPPT4_VOLTAGE | U16 | V | 0.1
26 | mppt4_current | PDF | O | 0x103F | MPPT4_CURRENT | S16 | A | 0.01
27 | mppt5_voltage | PDF | O | 0x1080 | MPPT5 Voltage | U16 | V | 0.1
28 | mppt5_current | PDF | O | 0x1081 | MPPT5 Current | S16 | A | 0.01
29 | mppt6_voltage | PDF | O | 0x1084 | MPPT6 Voltage | U16 | V | 0.1
30 | mppt6_current | PDF | O | 0x1085 | MPPT6 Current | S16 | A | 0.01
31 | mppt7_voltage | PDF | O | 0x1088 | MPPT7 Voltage | U16 | V | 0.1
32 | mppt7_current | PDF | O | 0x1089 | MPPT7 Current | S16 | A | 0.01
33 | mppt8_voltage | PDF | O | 0x108C | MPPT8 Voltage | U16 | V | 0.1
34 | mppt8_current | PDF | O | 0x108D | MPPT8 Current | S16 | A | 0.01
35 | mppt9_voltage | PDF | O | 0x1090 | MPPT9 Voltage | U16 | V | 0.1
36 | mppt9_current | PDF | O | 0x1091 | MPPT9 Current | S16 | A | 0.01
37 | string1_current | PDF | O | 0x1051 | STRING1_CURRENT | S16 | A | 0.01
38 | string2_current | PDF | O | 0x1053 | STRING2_CURRENT | S16 | A | 0.01
39 | string3_current | PDF | O | 0x1055 | STRING3_CURRENT | S16 | A | 0.01
40 | string4_current | PDF | O | 0x1057 | STRING4_CURRENT | S16 | A | 0.01
41 | string5_current | PDF | O | 0x1059 | STRING5_CURRENT | S16 | A | 0.01
42 | string6_current | PDF | O | 0x105B | STRING6_CURRENT | S16 | A | 0.01
43 | string7_current | PDF | O | 0x105D | STRING7_CURRENT | S16 | A | 0.01
44 | string8_current | PDF | O | 0x105F | STRING8_CURRENT | S16 | A | 0.01
45 | string9_current | PDF | O | 0x1061 | String9 input current | S16 | A | 0.01
46 | string10_current | PDF | O | 0x1063 | String10 input current | S16 | A | 0.01
47 | string11_current | PDF | O | 0x1065 | String11 input current | S16 | A | 0.01
48 | string12_current | PDF | O | 0x1067 | String12 input current | S16 | A | 0.01
49 | string13_current | PDF | O | 0x1069 | String13 input current | S16 | A | 0.01
50 | string14_current | PDF | O | 0x106B | String14 input current | S16 | A | 0.01
51 | string15_current | PDF | O | 0x106D | String15 input current | S16 | A | 0.01
52 | string16_current | PDF | O | 0x106F | String16 input current | S16 | A | 0.01
53 | string17_current | PDF | O | 0x1071 | String17 input current | S16 | A | 0.01
54 | string18_current | PDF | O | 0x1073 | String18 input current | S16 | A | 0.01
55 | string19_current | PDF | O | 0x1075 | String19 input current | S16 | A | 0.01
56 | string20_current | PDF | O | 0x1077 | String20 input current | S16 | A | 0.01
57 | string21_current | PDF | O | 0x1079 | String21 input current | S16 | A | 0.01
58 | string22_current | PDF | O | 0x107B | String22 input current | S16 | A | 0.01
59 | string23_current | PDF | O | 0x107D | String23 input current | S16 | A | 0.01
60 | string24_current | PDF | O | 0x107F | String24 input current | S16 | A | 0.01

## 3_MPPT_STRING
MPPT & String 매칭 — MPPT 9ch / String 24ch
MPPT 채널 수 | 9
String 채널 수 | 24
String 모니터링 | Yes
MPPT 채널 H01 매칭 (18개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | mppt1_voltage | PDF | O | 0x1010 | PV_VOLTAGE | U16 | V | 0.1
2 | mppt1_current | PDF | O | 0x1011 | MPPT1_CURRENT | S16 | A | 0.01
3 | mppt2_voltage | PDF | O | 0x1014 | MPPT2_VOLTAGE | U16 | V | 0.1
4 | mppt2_current | PDF | O | 0x1015 | MPPT2_CURRENT | S16 | A | 0.01
5 | mppt3_voltage | PDF | O | 0x1018 | MPPT3_VOLTAGE | U16 | V | 0.1
6 | mppt3_current | PDF | O | 0x1019 | MPPT3_CURRENT | S16 | A | 0.01
7 | mppt4_voltage | PDF | O | 0x103E | MPPT4_VOLTAGE | U16 | V | 0.1
8 | mppt4_current | PDF | O | 0x103F | MPPT4_CURRENT | S16 | A | 0.01
9 | mppt5_voltage | PDF | O | 0x1080 | MPPT5 Voltage | U16 | V | 0.1
10 | mppt5_current | PDF | O | 0x1081 | MPPT5 Current | S16 | A | 0.01
11 | mppt6_voltage | PDF | O | 0x1084 | MPPT6 Voltage | U16 | V | 0.1
12 | mppt6_current | PDF | O | 0x1085 | MPPT6 Current | S16 | A | 0.01
13 | mppt7_voltage | PDF | O | 0x1088 | MPPT7 Voltage | U16 | V | 0.1
14 | mppt7_current | PDF | O | 0x1089 | MPPT7 Current | S16 | A | 0.01
15 | mppt8_voltage | PDF | O | 0x108C | MPPT8 Voltage | U16 | V | 0.1
16 | mppt8_current | PDF | O | 0x108D | MPPT8 Current | S16 | A | 0.01
17 | mppt9_voltage | PDF | O | 0x1090 | MPPT9 Voltage | U16 | V | 0.1
18 | mppt9_current | PDF | O | 0x1091 | MPPT9 Current | S16 | A | 0.01
String 채널 H01 매칭 (24개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | string1_current | PDF | O | 0x1051 | STRING1_CURRENT | S16 | A | 0.01
2 | string2_current | PDF | O | 0x1053 | STRING2_CURRENT | S16 | A | 0.01
3 | string3_current | PDF | O | 0x1055 | STRING3_CURRENT | S16 | A | 0.01
4 | string4_current | PDF | O | 0x1057 | STRING4_CURRENT | S16 | A | 0.01
5 | string5_current | PDF | O | 0x1059 | STRING5_CURRENT | S16 | A | 0.01
6 | string6_current | PDF | O | 0x105B | STRING6_CURRENT | S16 | A | 0.01
7 | string7_current | PDF | O | 0x105D | STRING7_CURRENT | S16 | A | 0.01
8 | string8_current | PDF | O | 0x105F | STRING8_CURRENT | S16 | A | 0.01
9 | string9_current | PDF | O | 0x1061 | String9 input current | S16 | A | 0.01
10 | string10_current | PDF | O | 0x1063 | String10 input current | S16 | A | 0.01
11 | string11_current | PDF | O | 0x1065 | String11 input current | S16 | A | 0.01
12 | string12_current | PDF | O | 0x1067 | String12 input current | S16 | A | 0.01
13 | string13_current | PDF | O | 0x1069 | String13 input current | S16 | A | 0.01
14 | string14_current | PDF | O | 0x106B | String14 input current | S16 | A | 0.01
15 | string15_current | PDF | O | 0x106D | String15 input current | S16 | A | 0.01
16 | string16_current | PDF | O | 0x106F | String16 input current | S16 | A | 0.01
17 | string17_current | PDF | O | 0x1071 | String17 input current | S16 | A | 0.01
18 | string18_current | PDF | O | 0x1073 | String18 input current | S16 | A | 0.01
19 | string19_current | PDF | O | 0x1075 | String19 input current | S16 | A | 0.01
20 | string20_current | PDF | O | 0x1077 | String20 input current | S16 | A | 0.01
21 | string21_current | PDF | O | 0x1079 | String21 input current | S16 | A | 0.01
22 | string22_current | PDF | O | 0x107B | String22 input current | S16 | A | 0.01
23 | string23_current | PDF | O | 0x107D | String23 input current | S16 | A | 0.01
24 | string24_current | PDF | O | 0x107F | String24 input current | S16 | A | 0.01
MONITORING 전체 (183개)
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field
1 | POWER_FACTOR | 0x0000 | 03 | U16 |  | RO | power_factor
2 | START_BIT | 0x0001 | 03 | U16 |  | RO | temperature
3 | REGISTER_NUMBER | 0x0002 | 03 | U16 |  | RO | frequency
4 | READ_REGISTER_ADDRESS | 0x0003 | 03 | U16 |  | RO | reactive_power
5 | Write a single register address | 0x0006 | 03 | U16 |  | WO
6 | REG_0X07 | 0x0007 | 03 | U16 |  | RO
7 | PV_STRING_COUNT | 0x0008 | 03 | U16 |  | RO
8 | DC_LINK_OVER_VOLTAGE | 0x0009 | 03 | U16 |  | RO
9 | INTERNAL_COMMUNICATION_ERROR | 0x000A | 03 | U16 |  | RO
10 | SOFTWARE_INCOMPATIBILITY | 0x000B | 03 | U16 |  | RO | pv_power
11 | INTERNAL_STORAGE_ERROR | 0x000C | 03 | U16 |  | RO | r_voltage
12 | L2_VOLTAGE | 0x000D | 03 | U16 |  | RO | s_voltage
13 | L3_VOLTAGE | 0x000E | 03 | U16 |  | RO | t_voltage
14 | FREQUENCY | 0x000F | 03 | U16 |  | RO | frequency
15 | Write multiple register address | 0x0010 | 03 | U16 |  | WO | pv_power
16 | L1_VOLTAGE | 0x0026 | 03 | U16 |  | RO | r_voltage
17 | L1 Voltage | 0x1001 | 03 | U16 | V 0.1 | RO | r_voltage
18 | L1_CURRENT | 0x1002 | 03 | U16 | A 0.01 | RO | r_current
19 | L1_POWER | 0x1003 | 03 | S32 | W 0.1 | RO
20 | FREQUENCY | 0x1005 | 03 | U16 | Hz 0.01 | RO | frequency
21 | L2 Voltage | 0x1006 | 03 | U16 | V 0.1 | RO | s_voltage
22 | L2_CURRENT | 0x1007 | 03 | U16 | A 0.01 | RO | s_current
23 | L2_POWER | 0x1008 | 03 | S32 | W 0.1 | RO
24 | FREQUENCY | 0x100A | 03 | U16 | Hz 0.01 | RO | frequency
25 | L3 Voltage | 0x100B | 03 | U16 | V 0.1 | RO | t_voltage
26 | L3_CURRENT | 0x100C | 03 | U16 | A 0.01 | RO | t_current
27 | L3_POWER | 0x100D | 03 | S32 | W 0.1 | RO
28 | FREQUENCY | 0x100F | 03 | U16 | Hz 0.01 | RO | frequency
29 | PV_VOLTAGE | 0x1010 | 03 | U16 | V 0.1 | RO | mppt1_voltage
30 | MPPT1_CURRENT | 0x1011 | 03 | S16 | A 0.01 | RO | mppt1_current
31 | MPPT1_POWER | 0x1012 | 03 | U32 | W 0.1 | RO | mppt1_power
32 | MPPT2_VOLTAGE | 0x1014 | 03 | U16 | V 0.1 | RO | mppt2_voltage
33 | MPPT2_CURRENT | 0x1015 | 03 | S16 | A 0.01 | RO | mppt2_current
34 | MPPT2_POWER | 0x1016 | 03 | U32 | W 0.1 | RO | mppt2_power
35 | MPPT3_VOLTAGE | 0x1018 | 03 | U16 | V 0.1 | RO | mppt3_voltage
36 | MPPT3_CURRENT | 0x1019 | 03 | S16 | A 0.01 | RO | mppt3_current
37 | MPPT3_POWER | 0x101A | 03 | U32 | W 0.1 | RO | mppt3_power
38 | TEMPERATURE | 0x101C | 03 | S16 | °C 1 | RO | temperature
39 | CUMULATIVE_ENERGY | 0x1021 | 03 | U32 | kWh | RO | cumulative_energy
40 | TOTAL_GENERATION_TIME | 0x1023 | 03 | U32 |  | RO
41 | AC_POWER | 0x1037 | 03 | S32 | W 0.1 | RO | ac_power
42 | AC_POWER | 0x1039 | 03 | S32 |  | RO | ac_power
43 | PV_TODAY_PEAK_POWER | 0x103B | 03 | S32 | W 0.1 | RO
44 | Power Factor | 0x103D | 03 | S16 |  | RO | power_factor
45 | MPPT4_VOLTAGE | 0x103E | 03 | U16 | V 0.1 | RO | mppt4_voltage
46 | MPPT4_CURRENT | 0x103F | 03 | S16 | A 0.01 | RO | mppt4_current
47 | MPPT4_POWER | 0x1040 | 03 | U32 | W 0.1 | RO | mppt4_power
48 | PV_POWER | 0x1048 | 03 | U32 | W 0.1 | RO | pv_power
49 | CUMULATIVE_ENERGY | 0x104C | 03 | U16 |  | RO | cumulative_energy_low
50 | STRING1_VOLTAGE | 0x1050 | 03 | U16 | V 0.1 | RO | string1_voltage
51 | STRING1_CURRENT | 0x1051 | 03 | S16 | A 0.01 | RO | string1_current
52 | STRING2_VOLTAGE | 0x1052 | 03 | U16 | V 0.1 | RO | string2_voltage
53 | STRING2_CURRENT | 0x1053 | 03 | S16 | A 0.01 | RO | string2_current
54 | STRING3_VOLTAGE | 0x1054 | 03 | U16 | V 0.1 | RO | string3_voltage
55 | STRING3_CURRENT | 0x1055 | 03 | S16 | A 0.01 | RO | string3_current
56 | STRING4_VOLTAGE | 0x1056 | 03 | U16 | V 0.1 | RO | string4_voltage
57 | STRING4_CURRENT | 0x1057 | 03 | S16 | A 0.01 | RO | string4_current
58 | STRING5_VOLTAGE | 0x1058 | 03 | U16 | V 0.1 | RO | string5_voltage
59 | STRING5_CURRENT | 0x1059 | 03 | S16 | A 0.01 | RO | string5_current
60 | STRING6_VOLTAGE | 0x105A | 03 | U16 | V 0.1 | RO | string6_voltage
61 | STRING6_CURRENT | 0x105B | 03 | S16 | A 0.01 | RO | string6_current
62 | STRING7_VOLTAGE | 0x105C | 03 | U16 | V 0.1 | RO | string7_voltage
63 | STRING7_CURRENT | 0x105D | 03 | S16 | A 0.01 | RO | string7_current
64 | STRING8_VOLTAGE | 0x105E | 03 | U16 | V 0.1 | RO | string8_voltage
65 | STRING8_CURRENT | 0x105F | 03 | S16 | A 0.01 | RO | string8_current
66 | String9 input voltage | 0x1060 | 03 | U16 | V 0.1 | RO | string9_voltage
67 | String9 input current | 0x1061 | 03 | S16 | A 0.01 | RO | string9_current
68 | String10 input voltage | 0x1062 | 03 | U16 | V 0.1 | RO | string10_voltage
69 | String10 input current | 0x1063 | 03 | S16 | A 0.01 | RO | string10_current
70 | String11 input voltage | 0x1064 | 03 | U16 | V 0.1 | RO | string11_voltage
71 | String11 input current | 0x1065 | 03 | S16 | A 0.01 | RO | string11_current
72 | String12 input voltage | 0x1066 | 03 | U16 | V 0.1 | RO | string12_voltage
73 | String12 input current | 0x1067 | 03 | S16 | A 0.01 | RO | string12_current
74 | String13 input voltage | 0x1068 | 03 | U16 | V 0.1 | RO | string13_voltage
75 | String13 input current | 0x1069 | 03 | S16 | A 0.01 | RO | string13_current
76 | String14 input voltage | 0x106A | 03 | U16 | V 0.1 | RO | string14_voltage
77 | String14 input current | 0x106B | 03 | S16 | A 0.01 | RO | string14_current
78 | String15 input voltage | 0x106C | 03 | U16 | V 0.1 | RO | string15_voltage
79 | String15 input current | 0x106D | 03 | S16 | A 0.01 | RO | string15_current
80 | String16 input voltage | 0x106E | 03 | U16 | V 0.1 | RO | string16_voltage
81 | String16 input current | 0x106F | 03 | S16 | A 0.01 | RO | string16_current
82 | String17 input voltage | 0x1070 | 03 | U16 | V 0.1 | RO | string17_voltage
83 | String17 input current | 0x1071 | 03 | S16 | A 0.01 | RO | string17_current
84 | String18 input voltage | 0x1072 | 03 | U16 | V 0.1 | RO | string18_voltage
85 | String18 input current | 0x1073 | 03 | S16 | A 0.01 | RO | string18_current
86 | String19 input voltage | 0x1074 | 03 | U16 | V 0.1 | RO | string19_voltage
87 | String19 input current | 0x1075 | 03 | S16 | A 0.01 | RO | string19_current
88 | String20 input voltage | 0x1076 | 03 | U16 | V 0.1 | RO | string20_voltage
89 | String20 input current | 0x1077 | 03 | S16 | A 0.01 | RO | string20_current
90 | String21 input voltage | 0x1078 | 03 | U16 | V 0.1 | RO | string21_voltage
91 | String21 input current | 0x1079 | 03 | S16 | A 0.01 | RO | string21_current
92 | String22 input voltage | 0x107A | 03 | U16 | V 0.1 | RO | string22_voltage
93 | String22 input current | 0x107B | 03 | S16 | A 0.01 | RO | string22_current
94 | String23 input voltage | 0x107C | 03 | U16 | V 0.1 | RO | string23_voltage
95 | String23 input current | 0x107D | 03 | S16 | A 0.01 | RO | string23_current
96 | String24 input voltage | 0x107E | 03 | U16 | V 0.1 | RO | string24_voltage
97 | String24 input current | 0x107F | 03 | S16 | A 0.01 | RO | string24_current
98 | MPPT5 Voltage | 0x1080 | 03 | U16 | V 0.1 | RO | mppt5_voltage
99 | MPPT5 Current | 0x1081 | 03 | S16 | A 0.01 | RO | mppt5_current
100 | MPPT5 Power | 0x1082 | 03 | U32 | W 0.1 | RO | mppt5_power
101 | MPPT6 Voltage | 0x1084 | 03 | U16 | V 0.1 | RO | mppt6_voltage
102 | MPPT6 Current | 0x1085 | 03 | S16 | A 0.01 | RO | mppt6_current
103 | MPPT6 Power | 0x1086 | 03 | U32 | W 0.1 | RO | mppt6_power
104 | MPPT7 Voltage | 0x1088 | 03 | U16 | V 0.1 | RO | mppt7_voltage
105 | MPPT7 Current | 0x1089 | 03 | S16 | A 0.01 | RO | mppt7_current
106 | MPPT7 Power | 0x108A | 03 | U32 | W 0.1 | RO | mppt7_power
107 | MPPT8 Voltage | 0x108C | 03 | U16 | V 0.1 | RO | mppt8_voltage
108 | MPPT8 Current | 0x108D | 03 | S16 | A 0.01 | RO | mppt8_current
109 | MPPT8 Power | 0x108E | 03 | U32 | W 0.1 | RO | mppt8_power
110 | MPPT9 Voltage | 0x1090 | 03 | U16 | V 0.1 | RO | mppt9_voltage
111 | MPPT9 Current | 0x1091 | 03 | S16 | A 0.01 | RO | mppt9_current
112 | MPPT9 Power | 0x1092 | 03 | U32 | W 0.1 | RO | mppt9_power
113 | EXTERNAL_FAN_SPEED_DUTYPERCENTAGE | 0x120C | 03 | U16 |  | RO
114 | Q_REFERENCE_OUTPUT_REACTIVEPOWER | 0x1226 | 03 | S16 |  | RO
115 | L1_WATT_OF_GRID | 0x1300 | 03 | S32 | W 0.1 | RO
116 | L2_WATT_OF_GRID | 0x1302 | 03 | S32 | W 0.1 | RO
117 | L3_WATT_OF_GRID | 0x1304 | 03 | S32 | W 0.1 | RO
118 | CUMULATIVE_ENERGY | 0x1306 | 03 | U32 | Wh 10 | RO | cumulative_energy
119 | CUMULATIVE_ENERGY | 0x1308 | 03 | U32 | Wh 10 | RO | cumulative_energy
120 | L1_WATT_OF_LOAD | 0x130A | 03 | U32 | W 0.1 | RO
121 | L2_WATT_OF_LOAD | 0x130C | 03 | U32 | W 0.1 | RO
122 | L3_WATT_OF_LOAD | 0x130E | 03 | U32 | W 0.1 | RO
123 | CUMULATIVE_ENERGY | 0x1310 | 03 | U32 | Wh 10 | RO | cumulative_energy
124 | L1_CURRENT_OF_GRID | 0x131D | 03 | S32 | A 0.01 | RO
125 | L2_CURRENT_OF_GRID | 0x131F | 03 | S32 | A 0.01 | RO
126 | L3_CURRENT_OF_GRID | 0x1321 | 03 | S32 | A 0.01 | RO
127 | L1_CURRENT_OF_LOAD | 0x1326 | 03 | S32 | A 0.01 | RO
128 | L2_CURRENT_OF_LOAD | 0x1328 | 03 | S32 | A 0.01 | RO
129 | L3_CURRENT_OF_LOAD | 0x132A | 03 | S32 | A 0.01 | RO
130 | TODAY_IMPORT_ENERGY | 0x1332 | 03 | U32 | Wh 10 | RO
131 | TODAY_EXPORT_ENERGY | 0x1334 | 03 | U32 | Wh 10 | RO
132 | TODAY_LOAD_ENERGY | 0x1336 | 03 | U32 | Wh 10 | RO
133 | FREQUENCY | 0x1338 | 03 | U16 | Hz 0.01 | RO | frequency
134 | MPPT_NUMBER | 0x1A3B | 03 | U16 |  | RO
135 | POWER_FLOW_DIRECTION | 0x30B2 | 03 | U16 |  | RW
136 | MAXIMUM_FEED_IN_GRID_POWER | 0x30B9 | 03 | U32 |  | RW
137 | TRACKER_1_VOLTAGE | 0x8000 | 03 | U16 | V 0.1 | RO
138 | STRING_1_1_CURRENT | 0x8040 | 03 | S16 | A 0.01 | RO
139 | STRING_1_2_CURRENT | 0x8080 | 03 | STRINGING | A 0.01 | RO
140 | STRING_1_3_CURRENT | 0x80C0 | 03 | STRINGING | A 0.01 | RO
141 | STRING_1_4_CURRENT | 0x8100 | 03 | STRINGING | A 0.01 | RO
142 | TRACKER_2_VOLTAGE | 0x8140 | 03 | U16 | V 0.1 | RO
143 | STRING_2_1_CURRENT | 0x8180 | 03 | STRINGING | A 0.01 | RO
144 | STRING_2_2_CURRENT | 0x81C0 | 03 | STRINGING | A 0.01 | RO
145 | STRING_2_3_CURRENT | 0x8200 | 03 | STRINGING | A 0.01 | RO
146 | STRING_2_4_CURRENT | 0x8240 | 03 | STRINGING | A 0.01 | RO
147 | TRACKER_3_VOLTAGE | 0x8280 | 03 | U16 | V 0.1 | RO
148 | STRING_3_1_CURRENT | 0x82C0 | 03 | STRINGING | A 0.01 | RO
149 | STRING_3_2_CURRENT | 0x8300 | 03 | STRINGING | A 0.01 | RO
150 | STRING_3_3_CURRENT | 0x8340 | 03 | STRINGING | A 0.01 | RO
151 | STRING_3_4_CURRENT | 0x8380 | 03 | STRINGING | A 0.01 | RO
152 | TRACKER_4_VOLTAGE | 0x83C0 | 03 | U16 | V 0.1 | RO
153 | STRING_4_1_CURRENT | 0x8400 | 03 | STRINGING | A 0.01 | RO
154 | STRING_4_2_CURRENT | 0x8440 | 03 | STRINGING | A 0.01 | RO
155 | STRING_4_3_CURRENT | 0x8480 | 03 | STRINGING | A 0.01 | RO
156 | STRING_4_4_CURRENT | 0x84C0 | 03 | STRINGING | A 0.01 | RO
157 | TRACKER_5_VOLTAGE | 0x8500 | 03 | U16 | V 0.1 | RO
158 | STRING_5_1_CURRENT | 0x8540 | 03 | STRINGING | A 0.01 | RO
159 | STRING_5_2_CURRENT | 0x8580 | 03 | STRINGING | A 0.01 | RO
160 | STRING_5_3_CURRENT | 0x85C0 | 03 | STRINGING | A 0.01 | RO
161 | STRING_5_4_CURRENT | 0x8600 | 03 | STRINGING | A 0.01 | RO
162 | TRACKER_6_VOLTAGE | 0x8640 | 03 | U16 | V 0.1 | RO
163 | STRING_6_1_CURRENT | 0x8680 | 03 | STRINGING | A 0.01 | RO
164 | STRING_6_2_CURRENT | 0x86C0 | 03 | STRINGING | A 0.01 | RO
165 | STRING_6_3_CURRENT | 0x8700 | 03 | STRINGING | A 0.01 | RO
166 | STRING_6_4_CURRENT | 0x8740 | 03 | STRINGING | A 0.01 | RO
167 | TRACKER_7_VOLTAGE | 0x8780 | 03 | U16 | V 0.1 | RO
168 | STRING_7_1_CURRENT | 0x87C0 | 03 | STRINGING | A 0.01 | RO
169 | STRING_7_2_CURRENT | 0x8800 | 03 | STRINGING | A 0.01 | RO
170 | STRING_7_3_CURRENT | 0x8840 | 03 | STRINGING | A 0.01 | RO
171 | STRING_7_4_CURRENT | 0x8880 | 03 | STRINGING | A 0.01 | RO
172 | TRACKER_8_VOLTAGE | 0x88C0 | 03 | U16 | V 0.1 | RO
173 | STRING_8_1_CURRENT | 0x8900 | 03 | STRINGING | A 0.01 | RO
174 | STRING_8_2_CURRENT | 0x8940 | 03 | STRINGING | A 0.01 | RO
175 | STRING_8_3_CURRENT | 0x8980 | 03 | STRINGING | A 0.01 | RO
176 | STRING_8_4_CURRENT | 0x89C0 | 03 | STRINGING | A 0.01 | RO
177 | TRACKER_9_VOLTAGE | 0x8A00 | 03 | U16 | V 0.1 | RO
178 | STRING_9_1_CURRENT | 0x8A40 | 03 | STRINGING | A 0.01 | RO
179 | STRING_9_2_CURRENT | 0x8A80 | 03 | STRINGING | A 0.01 | RO
180 | STRING_9_3_CURRENT | 0x8AC0 | 03 | STRINGING | A 0.01 | RO
181 | STRING_9_4_CURRENT | 0x8B00 | 03 | STRINGING | A 0.01 | RO
182 | HISTORY_LOG_0 | 0xB600 | 03 | U16 |  | RO
183 | HISTORY_LOG_127 | 0xB77D | 03 | U16 |  | RO

## 4_DER
DER-AVM 매칭 — 33/33 (Sheet 4)
No | Field | Type | Status | Address | Scale | R/W | Description
1 | DER_POWER_FACTOR_SET | S16 | O | 0x07D0 | 0.001 | RW | Power factor [-1000,-800],[800,1000]
2 | DER_ACTION_MODE | U16 | O | 0x07D1 | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
3 | DER_REACTIVE_POWER_PCT | S16 | O | 0x07D2 | 0.1 | RW | Reactive power % [-484,484]
4 | DER_ACTIVE_POWER_PCT | U16 | O | 0x07D3 | 0.1 | RW | Active power % [0,1100]
5 | INVERTER_ON_OFF | U16 | O | 0x0834 | 1 | RW | On/Off: 0=ON, 1=OFF
6 | CLEAR_PV_INSULATION_WARNING | U16 | O | 0x0835 | 1 | WO | Clear PV insulation warning
7 | INVERTER_CONTROL | U16 | O | 0x6001 | 1 | WO | Inverter: 0=Power on, 1=Shut down
8 | IV_CURVE_SCAN | U16 | O | 0x600D | 1 | RW | IV scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
9 | POWER_FACTOR_DYNAMIC | S16 | O | 0x600F | 0.001 | RW | Dynamic power factor
10 | REACTIVE_POWER_DYNAMIC | S16 | O | 0x6010 | 0.01 | RW | Dynamic reactive power (%)
11 | POWER_DERATING_PCT | U16 | O | 0x3005 | 1 | RW | Active power derating [0-110]%
12 | DEA_L1_CURRENT_LOW | S32 | O | 0x03E8 | 0.1 | RO | DEA L1 current (low)
13 | DEA_L1_CURRENT_HIGH | S32 | O | 0x03E9 |  | RO | (high)
14 | DEA_L2_CURRENT_LOW | S32 | O | 0x03EA | 0.1 | RO | DEA L2 current (low)
15 | DEA_L2_CURRENT_HIGH | S32 | O | 0x03EB |  | RO | (high)
16 | DEA_L3_CURRENT_LOW | S32 | O | 0x03EC | 0.1 | RO | DEA L3 current (low)
17 | DEA_L3_CURRENT_HIGH | S32 | O | 0x03ED |  | RO | (high)
18 | DEA_L1_VOLTAGE_LOW | S32 | O | 0x03EE | 0.1 | RO | DEA L1 voltage (low)
19 | DEA_L1_VOLTAGE_HIGH | S32 | O | 0x03EF |  | RO | (high)
20 | DEA_L2_VOLTAGE_LOW | S32 | O | 0x03F0 | 0.1 | RO | DEA L2 voltage (low)
21 | DEA_L2_VOLTAGE_HIGH | S32 | O | 0x03F1 |  | RO | (high)
22 | DEA_L3_VOLTAGE_LOW | S32 | O | 0x03F2 | 0.1 | RO | DEA L3 voltage (low)
23 | DEA_L3_VOLTAGE_HIGH | S32 | O | 0x03F3 |  | RO | (high)
24 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | O | 0x03F4 | 0.1 | RO | DEA active power (low)
25 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | O | 0x03F5 |  | RO | (high)
26 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | O | 0x03F6 | 1 | RO | DEA reactive power (low)
27 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | O | 0x03F7 |  | RO | (high)
28 | DEA_POWER_FACTOR_LOW | S32 | O | 0x03F8 | 0.001 | RO | DEA power factor (low)
29 | DEA_POWER_FACTOR_HIGH | S32 | O | 0x03F9 |  | RO | (high)
30 | DEA_FREQUENCY_LOW | S32 | O | 0x03FA | 0.1 | RO | DEA frequency (low)
31 | DEA_FREQUENCY_HIGH | S32 | O | 0x03FB |  | RO | (high)
32 | DEA_STATUS_FLAG_LOW | S32 | O | 0x03FC | 1 | RO | DEA status flag (low)
33 | DEA_STATUS_FLAG_HIGH | S32 | O | 0x03FD |  | RO | (high)

## 5_IV
IV Scan 매핑 — data_points=64
IV Scan Command | 0x600D
Data Points | 64
Trackers | 9
Strings/Tracker | 0
IV Scan Command
Name | Address | Type | R/W | Description
IV_CURVE_SCAN | 0x600D | U16 | RW | W: 0=Stop, 1=Start / R: 0=Idle, 1=Running, 2=Finished
IV Data 레지스터 매핑
No | Type | Name | Address | Regs | Data Type | Scale
1 | Tracker Voltage | Tracker 1 voltage | 0x8000 | 64 | U16 | 0.1V
2 | Tracker Voltage | Tracker 2 voltage | 0x8140 | 64 | U16 | 0.1V
3 | Tracker Voltage | Tracker 3 voltage | 0x8280 | 64 | U16 | 0.1V
4 | Tracker Voltage | Tracker 4 voltage | 0x83C0 | 64 | U16 | 0.1V
5 | Tracker Voltage | Tracker 5 voltage | 0x8500 | 64 | U16 | 0.1V
6 | Tracker Voltage | Tracker 6 voltage | 0x8640 | 64 | U16 | 0.1V
7 | Tracker Voltage | Tracker 7 voltage | 0x8780 | 64 | U16 | 0.1V
8 | Tracker Voltage | Tracker 8 voltage | 0x88C0 | 64 | U16 | 0.1V
9 | Tracker Voltage | Tracker 9 voltage | 0x8A00 | 64 | U16 | 0.1V