## 1_REGISTER_MAP
Stage 2 — 레지스터맵 (MPPT=4, STR=8)
제조사 | test
용량 | 50kw
MPPT | 4
String/MPPT | 2
Total Strings | 8
H01 매칭 | 60/60
DER 매칭 | 33/33
총 레지스터 | 147
REVIEW | 0
INFO 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Total generation time | 0x1023 | U32 |  | RO
2 | DAILY_ENERGY | 0x1027 | U32 | Wh | RO | daily_energy | Today Energy
3 | L1-N phase voltage of grid | 0x131A | U16 | V 0.1 | RO
4 | L2-N phase voltage of grid | 0x131B | U16 | V 0.1 | RO
5 | L3-N phase voltage of grid | 0x131C | U16 | V 0.1 | RO
6 | L1-N phase voltage of load | 0x1323 | U16 | V 0.1 | RO
7 | L2-N phase voltage of load | 0x1324 | U16 | V 0.1 | RO
8 | L3-N phase voltage of load | 0x1325 | U16 | V 0.1 | RO
9 | Device Model name | 0x1A00 | STRINGING |  | RO |  | Ex.：PV 30KTL
10 | Device Serial number | 0x1A10 | STRINGING |  | RO |  | Ex.：1234-123456789
11 | Master firmware version | 0x1A1C | STRINGING |  | RO |  | Ex.：123456
12 | Slave firmware version | 0x1A26 | STRINGING |  | RO |  | Ex.：123456
13 | Nominal Voltage | 0x1A44 | U16 |  | RO |  | Ex.：2200 = 220V
14 | Nominal Frequency | 0x1A45 | U16 |  | RO |  | Ex.：5000 = 50Hz
15 | Nominal Active Power(Low word) | 0x1A46 | U16 | W 1 | RO |  | Ex.：1500 = 1500W
16 | Grid Phase Number | 0x1A48 | U16 |  | RO |  | 1=single phase2=split phase3=three phases
17 | Nominal Active Power(High word) | 0x1A4E | U16 | W 1 | RO |  | Ex.：1 = (1*65536)W
18 | EMS Firmware Version | 0x1A60 | STRINGING |  | RO |  | Ex.：123456
19 | LCD firmware version | 0x1A8E | STRINGING |  | RO |  | Ex.：123456
H01 MONITORING (122개)
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | POWER_FACTOR | 0x0000 | U16 |  | RO | power_factor
2 | TEMPERATURE | 0x0001 | U16 |  | RO | temperature
3 | FREQUENCY | 0x0002 | U16 |  | RO | frequency
4 | REACTIVE_POWER | 0x0003 | U16 |  | RO | reactive_power
5 | Write a single register address | 0x0006 | U16 |  | WO
6 | 0x07 | 0x0007 | U16 |  | RO
7 | Dc-link over voltage | 0x0009 | U16 |  | RO
8 | Internal communication error | 0x000A | U16 |  | RO
9 | PV_POWER | 0x000B | U16 |  | RO | pv_power
10 | Internal storage error | 0x000C | U16 |  | RO | r_voltage
11 | L2_VOLTAGE | 0x000D | U16 |  | RO | s_voltage
12 | L3_VOLTAGE | 0x000E | U16 |  | RO | t_voltage
13 | FREQUENCY | 0x000F | U16 |  | RO | frequency
14 | PV_POWER | 0x0010 | U16 |  | WO | pv_power
15 | L1_VOLTAGE | 0x0026 | U16 |  | RO | r_voltage
16 | L1 Voltage | 0x1001 | U16 | V 0.1 | RO | r_voltage
17 | L1 Current | 0x1002 | U16 | A 0.01 | RO | r_current
18 | L1 Power | 0x1003 | S32 | W 0.1 | RO
19 | FREQUENCY | 0x1005 | U16 | Hz 0.01 | RO | frequency
20 | L2 Voltage | 0x1006 | U16 | V 0.1 | RO | s_voltage
21 | L2 Current | 0x1007 | U16 | A 0.01 | RO | s_current
22 | L2 Power | 0x1008 | S32 | W 0.1 | RO
23 | FREQUENCY | 0x100A | U16 | Hz 0.01 | RO | frequency
24 | L3 Voltage | 0x100B | U16 | V 0.1 | RO | t_voltage
25 | L3 Current | 0x100C | U16 | A 0.01 | RO | t_current
26 | L3 Power | 0x100D | S32 | W 0.1 | RO
27 | FREQUENCY | 0x100F | U16 | Hz 0.01 | RO | frequency
28 | MPPT1 Voltage | 0x1010 | U16 | V 0.1 | RO | mppt1_voltage
29 | MPPT1 Current | 0x1011 | S16 | A 0.01 | RO | mppt1_current
30 | MPPT1 Power | 0x1012 | U32 | W 0.1 | RO | mppt1_power
31 | MPPT2 Voltage | 0x1014 | U16 | V 0.1 | RO | mppt2_voltage
32 | MPPT2 Current | 0x1015 | S16 | A 0.01 | RO | mppt2_current
33 | MPPT2 Power | 0x1016 | U32 | W 0.1 | RO | mppt2_power
34 | MPPT3 Voltage | 0x1018 | U16 | V 0.1 | RO | mppt3_voltage
35 | MPPT3 Current | 0x1019 | S16 | A 0.01 | RO | mppt3_current
36 | MPPT3 Power | 0x101A | U32 | W 0.1 | RO | mppt3_power
37 | TEMPERATURE | 0x101C | S16 | °C 1 | RO | temperature
38 | CUMULATIVE_ENERGY | 0x1021 | U32 | kWh | RO | cumulative_energy
39 | AC_POWER | 0x1037 | S32 | W 0.1 | RO | ac_power
40 | AC_POWER | 0x1039 | S32 |  | RO | ac_power
41 | PV Today Peak Power | 0x103B | S32 | W 0.1 | RO
42 | Power Factor | 0x103D | S16 |  | RO | power_factor
43 | MPPT4 Voltage | 0x103E | U16 | V 0.1 | RO | mppt4_voltage
44 | MPPT4 Current | 0x103F | S16 | A 0.01 | RO | mppt4_current
45 | MPPT4 Power | 0x1040 | U32 | W 0.1 | RO | mppt4_power
46 | PV_POWER | 0x1048 | U32 | W 0.1 | RO | pv_power
47 | CUMULATIVE_ENERGY_LOW | 0x104C | U16 |  | RO | cumulative_energy_low
48 | String1 input voltage | 0x1050 | U16 | V 0.1 | RO | string1_voltage
49 | String1 input current | 0x1051 | S16 | A 0.01 | RO | string1_current
50 | String2 input voltage | 0x1052 | U16 | V 0.1 | RO | string2_voltage
51 | String2 input current | 0x1053 | S16 | A 0.01 | RO | string2_current
52 | String3 input voltage | 0x1054 | U16 | V 0.1 | RO | string3_voltage
53 | String3 input current | 0x1055 | S16 | A 0.01 | RO | string3_current
54 | String4 input voltage | 0x1056 | U16 | V 0.1 | RO | string4_voltage
55 | String4 input current | 0x1057 | S16 | A 0.01 | RO | string4_current
56 | String5 input voltage | 0x1058 | U16 | V 0.1 | RO | string5_voltage
57 | String5 input current | 0x1059 | S16 | A 0.01 | RO | string5_current
58 | String6 input voltage | 0x105A | U16 | V 0.1 | RO | string6_voltage
59 | String6 input current | 0x105B | S16 | A 0.01 | RO | string6_current
60 | String7 input voltage | 0x105C | U16 | V 0.1 | RO | string7_voltage
61 | String7 input current | 0x105D | S16 | A 0.01 | RO | string7_current
62 | String8 input voltage | 0x105E | U16 | V 0.1 | RO | string8_voltage
63 | String8 input current | 0x105F | S16 | A 0.01 | RO | string8_current
64 | External fan speed dutypercentage | 0x120C | U16 |  | RO
65 | Q (Reference Output reactivepower) | 0x1226 | S16 |  | RO
66 | L1 watt of grid | 0x1300 | S32 | W 0.1 | RO
67 | L2 watt of grid | 0x1302 | S32 | W 0.1 | RO
68 | L3 watt of grid | 0x1304 | S32 | W 0.1 | RO
69 | CUMULATIVE_ENERGY | 0x1306 | U32 | Wh 10 | RO | cumulative_energy
70 | CUMULATIVE_ENERGY | 0x1308 | U32 | Wh 10 | RO | cumulative_energy
71 | L1 watt of load | 0x130A | U32 | W 0.1 | RO
72 | L2 watt of load | 0x130C | U32 | W 0.1 | RO
73 | L3 watt of load | 0x130E | U32 | W 0.1 | RO
74 | CUMULATIVE_ENERGY | 0x1310 | U32 | Wh 10 | RO | cumulative_energy
75 | L1 current of grid | 0x131D | S32 | A 0.01 | RO
76 | L2 current of grid | 0x131F | S32 | A 0.01 | RO
77 | L3 current of grid | 0x1321 | S32 | A 0.01 | RO
78 | L1 current of load | 0x1326 | S32 | A 0.01 | RO
79 | L2 current of load | 0x1328 | S32 | A 0.01 | RO
80 | L3 current of load | 0x132A | S32 | A 0.01 | RO
81 | Today import Energy | 0x1332 | U32 | Wh 10 | RO
82 | Today export Energy | 0x1334 | U32 | Wh 10 | RO
83 | Today load Energy | 0x1336 | U32 | Wh 10 | RO
84 | FREQUENCY | 0x1338 | U16 | Hz 0.01 | RO | frequency
85 | MPPT Number | 0x1A3B | U16 |  | RO
86 | Power flow direction | 0x30B2 | U16 |  | RW
87 | Maximum feed in grid power | 0x30B9 | U32 |  | RW
88 | String 1-3 current | 0x80C0 | STRINGING | A 0.01 | RO
89 | String 1-4 current | 0x8100 | STRINGING | A 0.01 | RO
90 | String 2-3 current | 0x8200 | STRINGING | A 0.01 | RO
91 | String 2-4 current | 0x8240 | STRINGING | A 0.01 | RO
92 | String 3-3 current | 0x8340 | STRINGING | A 0.01 | RO
93 | String 3-4 current | 0x8380 | STRINGING | A 0.01 | RO
94 | String 4-3 current | 0x8480 | STRINGING | A 0.01 | RO
95 | String 4-4 current | 0x84C0 | STRINGING | A 0.01 | RO
96 | Tracker 5 voltage | 0x8500 | U16 | V 0.1 | RO
97 | String 5-1 current | 0x8540 | STRINGING | A 0.01 | RO
98 | String 5-2 current | 0x8580 | STRINGING | A 0.01 | RO
99 | String 5-3 current | 0x85C0 | STRINGING | A 0.01 | RO
100 | String 5-4 current | 0x8600 | STRINGING | A 0.01 | RO
101 | Tracker 6 voltage | 0x8640 | U16 | V 0.1 | RO
102 | String 6-1 current | 0x8680 | STRINGING | A 0.01 | RO
103 | String 6-2 current | 0x86C0 | STRINGING | A 0.01 | RO
104 | String 6-3 current | 0x8700 | STRINGING | A 0.01 | RO
105 | String 6-4 current | 0x8740 | STRINGING | A 0.01 | RO
106 | Tracker 7 voltage | 0x8780 | U16 | V 0.1 | RO
107 | String 7-1 current | 0x87C0 | STRINGING | A 0.01 | RO
108 | String 7-2 current | 0x8800 | STRINGING | A 0.01 | RO
109 | String 7-3 current | 0x8840 | STRINGING | A 0.01 | RO
110 | String 7-4 current | 0x8880 | STRINGING | A 0.01 | RO
111 | Tracker 8 voltage | 0x88C0 | U16 | V 0.1 | RO
112 | String 8-1 current | 0x8900 | STRINGING | A 0.01 | RO
113 | String 8-2 current | 0x8940 | STRINGING | A 0.01 | RO
114 | String 8-3 current | 0x8980 | STRINGING | A 0.01 | RO
115 | String 8-4 current | 0x89C0 | STRINGING | A 0.01 | RO
116 | Tracker 9 voltage | 0x8A00 | U16 | V 0.1 | RO
117 | String 9-1 current | 0x8A40 | STRINGING | A 0.01 | RO
118 | String 9-2 current | 0x8A80 | STRINGING | A 0.01 | RO
119 | String 9-3 current | 0x8AC0 | STRINGING | A 0.01 | RO
120 | String 9-4 current | 0x8B00 | STRINGING | A 0.01 | RO
121 | history log 0 | 0xB600 | U16 |  | RO
122 | history log 127 | 0xB77D | U16 |  | RO
STATUS 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Inverter Mode | 0x101D | U16 |  | RO | inverter_status | Inverter Mode Table
ALARM 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | L1_VOLTAGE | 0x0004 | U16 |  | RO | r_voltage | GFCI abnormal
2 | L2_VOLTAGE | 0x0005 | STRINGING |  | RO | s_voltage | PV string reverse
3 | Error Code1 | 0x101E | U16 |  | RO |  | Error Code Table 1
4 | Error Code2 | 0x101F | U16 |  | RO |  | Error Code Table 2
5 | Error Code3 | 0x1020 | U16 |  | RO |  | Error Code Table 3

## 2_REVIEW
REVIEW — 0개 미결
REVIEW 항목 없음 — 모든 레지스터 자동 분류 완료

## 3_SUMMARY
Stage 2 Summary
제조사 | test
용량 | 50kw
MPPT | 4 (PDF max 9개)
String | 8 (2/MPPT)
H01 매칭 | 60/60
DER 매칭 | 33/33
총 레지스터 | 147
REVIEW 미결 | 0
REVIEW 자동 처리 | 0
카테고리별 수량
INFO | 19
MONITORING | 122
STATUS | 1
ALARM | 5
H01 매칭 상태
No | H01 Field | Source | Status | Address | Definition
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY
10 | pv_voltage | HANDLER | O | - | -
11 | pv_current | HANDLER | O | - | -
12 | pv_power | PDF | O | 0x1048 | PV_POWER
13 | cumulative_energy | PDF | O | 0x1021 | CUMULATIVE_ENERGY
14 | cumulative_energy_low | PDF | O | 0x104C | CUMULATIVE_ENERGY_LOW
15 | status | PDF | O | 0x101D | Inverter Mode
16 | alarm1 | PDF | O | 0x101E | Error Code1
17 | alarm2 | PDF | O | 0x101F | Error Code2
18 | alarm3 | PDF | O | 0x1020 | Error Code3
19 | mppt1_voltage | PDF | O | 0x1010 | MPPT1 Voltage
20 | mppt1_current | PDF | O | 0x1011 | MPPT1 Current
21 | mppt2_voltage | PDF | O | 0x1014 | MPPT2 Voltage
22 | mppt2_current | PDF | O | 0x1015 | MPPT2 Current
23 | mppt3_voltage | PDF | O | 0x1018 | MPPT3 Voltage
24 | mppt3_current | PDF | O | 0x1019 | MPPT3 Current
25 | mppt4_voltage | PDF | O | 0x103E | MPPT4 Voltage
26 | mppt4_current | PDF | O | 0x103F | MPPT4 Current
27 | mppt5_voltage | PDF | O | 0x1080 | MPPT5 Voltage
28 | mppt5_current | PDF | O | 0x1081 | MPPT5 Current
29 | mppt6_voltage | PDF | O | 0x1084 | MPPT6 Voltage
30 | mppt6_current | PDF | O | 0x1085 | MPPT6 Current
31 | mppt7_voltage | PDF | O | 0x1088 | MPPT7 Voltage
32 | mppt7_current | PDF | O | 0x1089 | MPPT7 Current
33 | mppt8_voltage | PDF | O | 0x108C | MPPT8 Voltage
34 | mppt8_current | PDF | O | 0x108D | MPPT8 Current
35 | mppt9_voltage | PDF | O | 0x1090 | MPPT9 Voltage
36 | mppt9_current | PDF | O | 0x1091 | MPPT9 Current
37 | string1_current | PDF | O | 0x1051 | String1 input current
38 | string2_current | PDF | O | 0x1053 | String2 input current
39 | string3_current | PDF | O | 0x1055 | String3 input current
40 | string4_current | PDF | O | 0x1057 | String4 input current
41 | string5_current | PDF | O | 0x1059 | String5 input current
42 | string6_current | PDF | O | 0x105B | String6 input current
43 | string7_current | PDF | O | 0x105D | String7 input current
44 | string8_current | PDF | O | 0x105F | String8 input current
45 | string9_current | PDF | O | 0x1061 | String9 input current
46 | string10_current | PDF | O | 0x1063 | String10 input current
47 | string11_current | PDF | O | 0x1065 | String11 input current
48 | string12_current | PDF | O | 0x1067 | String12 input current
49 | string13_current | PDF | O | 0x1069 | String13 input current
50 | string14_current | PDF | O | 0x106B | String14 input current
51 | string15_current | PDF | O | 0x106D | String15 input current
52 | string16_current | PDF | O | 0x106F | String16 input current
53 | string17_current | PDF | O | 0x1071 | String17 input current
54 | string18_current | PDF | O | 0x1073 | String18 input current
55 | string19_current | PDF | O | 0x1075 | String19 input current
56 | string20_current | PDF | O | 0x1077 | String20 input current
57 | string21_current | PDF | O | 0x1079 | String21 input current
58 | string22_current | PDF | O | 0x107B | String22 input current
59 | string23_current | PDF | O | 0x107D | String23 input current
60 | string24_current | PDF | O | 0x107F | String24 input current

## H01_MAPPING
H01_MAPPING — H01 필드별 레지스터 수동 매핑
※ D열에서 매핑할 레지스터명을 선택/입력하세요. E~G열은 추천 후보, H열은 전체 목록(드롭다운용).
No | H01 Field | 설명 | 매칭된 레지스터 (주소) | 추천 후보 1 | 추천 후보 2 | 추천 후보 3 | 전체 레지스터 목록
1 | pv_voltage | HANDLER 계산 (평균 MPPT 전압) | HANDLER | DC_LINK_OVER_VOLTAGE (0x0009) | MPPT1_VOLTAGE (0x1010) | MPPT2_VOLTAGE (0x1014) | POWER_FACTOR
2 | pv_current | HANDLER 계산 (합산 MPPT 전류) | HANDLER | MPPT1_CURRENT (0x1011) | MPPT2_CURRENT (0x1015) | MPPT3_CURRENT (0x1019) | TEMPERATURE
3 | pv_power | HANDLER 계산 (합산 MPPT 전력) | PV_POWER (0x1048) | PV_TODAY_PEAK_POWER (0x103B) |  |  | FREQUENCY
4 | r_voltage | R상(L1) 전압 | DEA_L1_VOLTAGE (0x03EE~0x03EF); INTERNAL_STORAGE_ERROR (0x000C); L1_VOLTAGE (0x0026) | TRACKER_5_VOLTAGE (0x8500) | TRACKER_6_VOLTAGE (0x8640) |  | REACTIVE_POWER
5 | s_voltage | S상(L2) 전압 | DEA_L2_VOLTAGE (0x03F0~0x03F1); L2_VOLTAGE (0x000D) | L2_N_PHASE_VOLTAGE_OF_GRID (0x131B) | L2_N_PHASE_VOLTAGE_OF_LOAD (0x1324) |  | WRITE_A_SINGLE_REGISTER_ADDRESS
6 | t_voltage | T상(L3) 전압 | DEA_L3_VOLTAGE (0x03F2~0x03F3); L3_VOLTAGE (0x000E) | L3_N_PHASE_VOLTAGE_OF_GRID (0x131C) | L3_N_PHASE_VOLTAGE_OF_LOAD (0x1325) |  | REG_0X07
7 | r_current | R상(L1) 전류 | DEA_L1_CURRENT (0x03E8~0x03E9); L1_CURRENT (0x1002) | L1_CURRENT_OF_GRID (0x131D) | L1_CURRENT_OF_LOAD (0x1326) |  | DC_LINK_OVER_VOLTAGE
8 | s_current | S상(L2) 전류 | DEA_L2_CURRENT (0x03EA~0x03EB); L2_CURRENT (0x1007) | L2_CURRENT_OF_GRID (0x131F) | L2_CURRENT_OF_LOAD (0x1328) |  | INTERNAL_COMMUNICATION_ERROR
9 | t_current | T상(L3) 전류 | DEA_L3_CURRENT (0x03EC~0x03ED); L3_CURRENT (0x100C) | L3_CURRENT_OF_GRID (0x1321) | L3_CURRENT_OF_LOAD (0x132A) |  | PV_POWER
10 | ac_power | AC 출력 전력 | DEA_TOTAL_ACTIVE_POWER (0x03F4~0x03F5); AC_POWER (0x1037) | REACTIVE_POWER (0x0003) | Q_REFERENCE_OUTPUT_REACTIVEPOWER (0x1226) |  | INTERNAL_STORAGE_ERROR
11 | power_factor | 역률 | DEA_POWER_FACTOR (0x03F8~0x03F9); POWER_FACTOR (0x0000) |  |  |  | L2_VOLTAGE
12 | frequency | 계통 주파수 | DEA_FREQUENCY (0x03FA~0x03FB); FREQUENCY (0x0002) | NOMINAL_FREQUENCY (0x1A45) |  |  | L3_VOLTAGE
13 | cumulative_energy | 누적 발전량 | CUMULATIVE_ENERGY (0x1021) | CUMULATIVE_ENERGY_LOW (0x104C) |  |  | L1_VOLTAGE
14 | status | 인버터 상태 | INVERTER_MODE (0x101D) |  |  |  | L1_CURRENT
15 | alarm1 | 경보 코드 1 | ERROR_CODE1 (0x101E) | ERROR_CODE2 (0x101F) | ERROR_CODE3 (0x1020) |  | L1_POWER
16 | alarm2 | 경보 코드 2 | ERROR_CODE2 (0x101F) | ERROR_CODE1 (0x101E) | ERROR_CODE3 (0x1020) |  | L2_CURRENT
17 | alarm3 | 경보 코드 3 | ERROR_CODE3 (0x1020) | ERROR_CODE1 (0x101E) | ERROR_CODE2 (0x101F) |  | L2_POWER
L3_CURRENT
L3_POWER
MPPT1_VOLTAGE
MPPT1_CURRENT
MPPT1_POWER
MPPT2_VOLTAGE
MPPT2_CURRENT
MPPT2_POWER
MPPT3_VOLTAGE
MPPT3_CURRENT
MPPT3_POWER
CUMULATIVE_ENERGY
AC_POWER
PV_TODAY_PEAK_POWER
MPPT4_VOLTAGE
MPPT4_CURRENT
MPPT4_POWER
CUMULATIVE_ENERGY_LOW
STRING1_INPUT_VOLTAGE
STRING1_INPUT_CURRENT
STRING2_INPUT_VOLTAGE
STRING2_INPUT_CURRENT
STRING3_INPUT_VOLTAGE
STRING3_INPUT_CURRENT
STRING4_INPUT_VOLTAGE
STRING4_INPUT_CURRENT
STRING5_INPUT_VOLTAGE
STRING5_INPUT_CURRENT
STRING6_INPUT_VOLTAGE
STRING6_INPUT_CURRENT
STRING7_INPUT_VOLTAGE
STRING7_INPUT_CURRENT
STRING8_INPUT_VOLTAGE
STRING8_INPUT_CURRENT
EXTERNAL_FAN_SPEED_DUTYPERCENTAGE
Q_REFERENCE_OUTPUT_REACTIVEPOWER
L1_WATT_OF_GRID
L2_WATT_OF_GRID
L3_WATT_OF_GRID
L1_WATT_OF_LOAD
L2_WATT_OF_LOAD
L3_WATT_OF_LOAD
L1_CURRENT_OF_GRID
L2_CURRENT_OF_GRID
L3_CURRENT_OF_GRID
L1_CURRENT_OF_LOAD
L2_CURRENT_OF_LOAD
L3_CURRENT_OF_LOAD
TODAY_IMPORT_ENERGY
TODAY_EXPORT_ENERGY
TODAY_LOAD_ENERGY
MPPT_NUMBER
POWER_FLOW_DIRECTION
MAXIMUM_FEED_IN_GRID_POWER
STRING_1_3_CURRENT
STRING_1_4_CURRENT
STRING_2_3_CURRENT
STRING_2_4_CURRENT
STRING_3_3_CURRENT
STRING_3_4_CURRENT
STRING_4_3_CURRENT
STRING_4_4_CURRENT
TRACKER_5_VOLTAGE
STRING_5_1_CURRENT
STRING_5_2_CURRENT
STRING_5_3_CURRENT
STRING_5_4_CURRENT
TRACKER_6_VOLTAGE
STRING_6_1_CURRENT
STRING_6_2_CURRENT
STRING_6_3_CURRENT
STRING_6_4_CURRENT
TRACKER_7_VOLTAGE
STRING_7_1_CURRENT
STRING_7_2_CURRENT
STRING_7_3_CURRENT
STRING_7_4_CURRENT
TRACKER_8_VOLTAGE
STRING_8_1_CURRENT
STRING_8_2_CURRENT
STRING_8_3_CURRENT
STRING_8_4_CURRENT
TRACKER_9_VOLTAGE
STRING_9_1_CURRENT
STRING_9_2_CURRENT
STRING_9_3_CURRENT
STRING_9_4_CURRENT
HISTORY_LOG_0
HISTORY_LOG_127
TOTAL_GENERATION_TIME
DAILY_ENERGY
L1_N_PHASE_VOLTAGE_OF_GRID
L2_N_PHASE_VOLTAGE_OF_GRID
L3_N_PHASE_VOLTAGE_OF_GRID
L1_N_PHASE_VOLTAGE_OF_LOAD
L2_N_PHASE_VOLTAGE_OF_LOAD
L3_N_PHASE_VOLTAGE_OF_LOAD
DEVICE_MODEL_NAME
DEVICE_SERIAL_NUMBER
MASTER_FIRMWARE_VERSION
SLAVE_FIRMWARE_VERSION
NOMINAL_VOLTAGE
NOMINAL_FREQUENCY
NOMINAL_ACTIVE_POWER_LOW_WORD
GRID_PHASE_NUMBER
NOMINAL_ACTIVE_POWER_HIGH_WORD
EMS_FIRMWARE_VERSION
LCD_FIRMWARE_VERSION
INVERTER_MODE
ERROR_CODE1
ERROR_CODE2
ERROR_CODE3